## README
ERCOT Drought Risk Analysis
This spreadsheet-based calculator is designed to help ERCOT evaluate risk of drought affecting generation supplies.
The methodologies contained herein are developed for this specific purpose, which is to provide early warning of possible outages or derating of generation units.
Guidance & Instructions
This spreadsheet is intended to allow users to understand the methodology behind ERCOT's drought risk analysis. The spreadsheets are for demo purposes only and are not intended to reflect conditions at any specific reservor or generating unit. The spreadsheets included in this workbook provide example calculations for a drainage-fed and off-channel reservoir. Separate methodologies are required for the two types of reservoirs due to their different modes of operation and information available. Additional explanation of the methodology behind the spreadsheet is available in Appendix 3 of ERCOT's report, Retrospective Analysis of the 2010-2015 Drought in ERCOT.
The following color conventions are used throughout the model:
Cells shown in this color may be used by the user to input updated information and select from different options.
Cells shown in this color contain data input information that are set by the user when initially developing the reservoir prediction.
Cells shown in this color contain calculations based on historical reservoir data and future reservoir storage predictions. These cells should not be modified.
Cells shown in this color contain model assumptions and other internal calculations. These cells should not be modified.
Yellow boxes contain user tips and other exlanatory information.
1
Please read before using the model:
Prediction of drought risk is an inexact science with current knowledge and understanding. Communications should be begun with at risk generators as soon as possible to determine if there are mitigating circumstances which could alter the inputs for the prediction.
User tips...
Electric Reliability Council of Texas

## Drainage-Fed Reservoir
[5 empty] | Historical Data |  |  |  |  | Reservoir Storage Predictions |  |  | All values are in acre-feet | [6 empty] | Percentile lookup for probability fit: | Calculation of Drought Fit | [23 empty] | Lake Bathymetry
| Risk | Average | Worst | Drought Fit | Year | Month | Elevation (ft) | Storage (Acre-ft) | Change (Acre-ft) |  | Reservoir Characteristics |  | Predicted Reservoir Storage |  |  |  | Is Prediction At Risk Level? |  |  |  | Lookup table for exceedence probability calculations | [7 empty] | Historical Monthly Changes in Storage | [15 empty] | Elevation (ft) | Volume (acre-ft)
| Months to Empty | 45 | 8 | 29 | 1999-12-01 | 12 | 45.1 | 77212.7501 |  | Date | Full Storage | At-Risk Storage | Average | Worst | Drought fit | Probability Fit | Average | Worst | Drought Fit | 1 | Month (#) | Month | 0.1 | 0.25 | 0.5 | 0.75 | 0.95 |  | Month/Year | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 0.01 | 0
| Months to At Risk | 45 | 6 | 20 | 2000-01-01 | 1 | 45.3 | 78120.9814 | 908.2313 | 2015-12-01 | 100000 | 20000 | 100000 | 100000 | 100000 | 100000 | No | No | No |  | 1 | JAN | -4732.6714 | -2365.4574 | 4643.3512 | 8188.8499 | 11902.7098 |  | 1 | 908.2313 | 9306.4596 | 4643.3512 | -5209.9383 | 7843.3363 | -1432.0444 | 5037.872 | 14550.214 | -9287.9467 | 2211.3566 | -3298.8703 | 10768.0651 | 8534.3635 | 5717.7267 | -4016.7712 | 0.1 | 0
[5 empty] | 2000-02-01 | 2 | 47.7 | 89156.8379 | 11035.8565 | 2016-01-01 | 100000 | 20000 | 99522.345 | 99522.345 | 99522.345 | 99522.345 | No | No | No |  | 2 | FEB | -4833.5623 | 483.5896 | 3189.4844 | 8100.6893 | 14981.1959 |  | 2 | 11035.8565 | 18865.109 | 9445.1826 | 1885.961 | 3269.1599 | -1426.3213 | 13316.6617 | -7105.0562 | -918.7817 | -8659.8487 | 4721.3845 | 1903.0059 | 3189.4844 | 6756.1959 | 3119.364 | 0.2 | 0
| Generators at Risk | MW | Cap Fctr | MWh (2015) | 2000-03-01 | 3 | 50.1 | 95100 | 5943.1621 | 2016-02-01 | 100000 | 20000 | 97141.6343 | 97141.6343 | 97141.6343 | 97141.6343 | No | No | No |  | 3 | MAR | -3380.0388 | -8.7215 | 4674.0022 | 9437.0832 | 15471.0376 |  | 3 | 5943.1621 | 6635.5877 | -1000 | 1420.9714 | 4674.0022 | 2858.3657 | 15295.8794 | 4721.3845 | 15879.7402 | 12238.5787 | -474.6939 | -7555.2653 | 457.2509 | -4966.7314 | 12736.5383 | 0.3 | 0
| Generator 2 | 600 | 66.5% | 3495000 | 2000-04-01 | 4 | 50.4 | 100000 | 4900 | 2016-03-01 | 100000 | 20000 | 101732.619 | 89586.3691 | 97141.6343 | 93761.5955 | No | No | No |  | 4 | APR | -3438.0512 | -216.3681 | 1000 | 4287.4017 | 11602.345 |  | 4 | 4900 | 0 | 1000 | 2858.3657 | -432.7361 | -5223.3005 | 10516.3283 | 951.6274 | 476.6846 | 10501.3885 | 2858.3657 | -5115.8057 | 3674.8034 | 14136.384 | -921.4193 | 0.4 | 0
[5 empty] | 2000-05-01 | 5 | 49.3 | 96667.2639 | -3332.7361 | 2016-04-01 | 100000 | 20000 | 104411.3314 | 84363.0686 | 97141.6343 | 90323.5443 | No | No | No |  | 5 | MAY | -6900.8858 | -4645.0309 | -952.971 | 6818.9758 | 12680.321 |  | 5 | -3332.7361 | -7105.0562 | -1908.3308 | -7574.0022 | 3332.7361 | 0 | -6594.6302 | -1426.3213 | -952.971 | 11900 | 0 | 10768.0651 | -5957.3256 | 10305.2155 | 14501.07 | 0.5 | 0
[5 empty] | 2000-06-01 | 6 | 47.9 | 90088.4344 | -6578.8295 | 2016-05-01 | 100000 | 20000 | 105475.0456 | 76789.0664 | 94093.7792 | 83422.6585 | No | No | No |  | 6 | JUN | -6128.5956 | -4008.8957 | -455.0861 | 2383.3483 | 5072.2007 |  | 6 | -6578.8295 | -2340.1264 | 1908.3308 | 7574.0022 | 0 | -1881.7557 | -2794.4909 | 2858.3657 | -6134.3685 | 4000 | -5223.3005 | -6119.9363 | -455.0861 | 2858.3657 | 1432.0444 | 0.6 | 0.024883
[5 empty] | 2000-07-01 | 7 | 47.1 | 86373.5692 | -3714.8651 | 2016-06-01 | 100000 | 20000 | 104748.5933 | 70210.2369 | 91390.1612 | 77294.0629 | No | No | No |  | 7 | JUL | -11772.7929 | -5930.0164 | -4194.0629 | -3253.3219 | 1566.9901 |  | 7 | -3714.8651 | -5105.0314 | -3332.7361 | -2858.3657 | -6165.2981 | -4203.2945 | -4160.3215 | 0 | -4194.0629 | -11772.7929 | 5223.3005 | -15167.7615 | -3173.9076 | -11772.7929 | -5694.7347 | 0.7 | 0.024883
[5 empty] | 2000-08-01 | 8 | 46.1 | 81771.2252 | -4602.344 | 2016-07-01 | 100000 | 20000 | 99675.749 | 55042.4754 | 85813.3672 | 65521.27 | No | No | No |  | 8 | AUG | -14107.9048 | -11745.1005 | -8563.2378 | -5919.5183 | 1562.9815 |  | 8 | -4602.344 | -7328.8046 | -7857.2639 | -13041.6343 | 5209.9383 | -9660.6699 | -11966.8856 | 0 | -8563.2378 | -5127.2071 | -10900 | -11523.3154 | -6711.8294 | -15527.1723 | -14818.7519 | 0.8 | 0.049766
[5 empty] | 2000-09-01 | 9 | 40.2 | 56120.5584 | -25650.6669 | 2016-08-01 | 100000 | 20000 | 91514.4705 | 39515.3031 | 74414.7148 | 51413.3652 | No | No | No |  | 9 | SEPT | -8293.0278 | -7551.6697 | -3360.214 | -499.1664 | 8286.3342 |  | 9 | -25650.6669 | 909.998 | -3360.214 | -7793.4159 | -2850.8261 | -7674.1316 | -8626.1023 | -1908.3308 | -3346.0635 | 8857.3007 | 8041.6343 | -7429.2077 | 2220.4141 | -6204.9617 | -5437.668 | 0.9 | 0.074649
[5 empty] | 2000-10-01 | 10 | 40.8 | 58487.4589 | 2366.9006 | 2016-09-01 | 100000 | 20000 | 87497.6544 | 13864.6362 | 67230.3563 | 43120.3374 | No | Yes | No |  | 10 | OCT | -9923.7484 | -5124.2585 | 0 | 2545.648 | 9117.662 |  | 10 | 2366.9006 | -455.0861 | 923.7832 | 2724.3953 | -7036.9762 | -5256.8478 | -850.6271 | -4991.6692 | -12806.0117 | 8042.6993 | 0 | 3210.7097 | 893.5503 | 11625.9082 | -11848.2632 | 1 | 0.099532
[5 empty] | 2000-11-01 | 11 | 41.7 | 62200.5823 | 3713.1233 | 2016-10-01 | 100000 | 20000 | 86600.4854 | 1058.6245 | 63066.8956 | 33196.589 | No | Yes | No |  | 11 | NOV | -5169.991 | -3120.0109 | -893.5503 | 3112.1355 | 12391.3556 |  | 11 | 3713.1233 | -1363.1432 | 0 | 5496.5413 | 9887.8023 | -5987.877 | 18232.98 | -3943.1621 | -424.6541 | -3332.7361 | -6119.9363 | 2511.1476 | -893.5503 | -1361.5507 | -2907.2858 | 1.1 | 0.1493
[5 empty] | 2000-12-01 | 12 | 42.4 | 65192.8436 | 2992.2614 | 2016-11-01 | 100000 | 20000 | 87500.9986 | -5061.3118 | 60468.4383 | 28026.598 | No | Yes | No |  | 12 | DEC | -6284.6123 | -4129.1928 | 955.3598 | 4889.3948 | 9890.4225 |  | 12 | 2992.2614 | 8698.716 | 12671.071 | -3214.0191 | 955.3598 | -6662.5361 | 4593.5354 | 3738.1059 | 5185.2543 | -473.4498 | -4648.1288 | 6509.1321 | -5717.7267 | -3610.2568 | -7700.4081 | 1.2 | 0.19906
| Reservoir Details |  |  |  | 2001-01-01 | 1 | 44.5 | 74499.3033 | 9306.4596 | 2016-12-01 | 100000 | 20000 | 88388.7927 | -12761.7199 | 56937.4291 | 21741.9857 | No | Yes | No | [25 empty] | 1.3 | 0.24883
| Full (Conservation) | 100000 | Acre-feet |  | 2001-02-01 | 2 | 48.6 | 93364.4123 | 18865.109 | 2017-01-01 | 100000 | 20000 | 91473.8197 | -22049.6666 | 55973.4398 | 17009.3142 | No | Yes | No |  | Monthly Changes in Storage - Statistics |  |  |  |  | Reservoir storage: | 100000 | Dr. fit % of Storage | [16 empty] | 1.4 | 0.32348
| At-Risk Level | 20000 | Acre-feet |  | 2001-03-01 | 3 | 51.2 | 100000 | 6635.5877 | 2017-02-01 | 100000 | 20000 | 95433.6435 | -30709.5153 | 55973.4398 | 12175.752 | No | Yes | No |  | Month (#) | Month | Max | Average | Min | 30th Percentile | Drought Fit | [17 empty] | 1.5 | 0.39813
[5 empty] | 2001-04-01 | 4 | 50.4 | 100000 | 0 | 2017-03-01 | 100000 | 20000 | 100024.6282 | -38264.7805 | 55973.4398 | 8795.7131 | No | Yes | No |  | 1 | JAN | 14550.214 | 3085.027 | -9287.9467 | -963.9893 | -963.9893 | 0.964% | [16 empty] | 1.6 | 0.47278
| At-Risk Level |  | Reasons |  | 2001-05-01 | 5 | 48.5 | 92894.9438 | -7105.0562 | 2017-04-01 | 100000 | 20000 | 102703.3406 | -43488.081 | 55973.4398 | 5357.662 | No | Yes | No |  | 2 | FEB | 18865.109 | 3959.8238 | -8659.8487 | 1889.37 | 0 | 0% | [16 empty] | 1.7 | 0.57231
| 20% | Set at default level of 20% for drainage-fed reservoirs |  |  | 2001-06-01 | 6 | 48 | 90554.8174 | -2340.1264 | 2017-05-01 | 100000 | 20000 | 103767.0548 | -51062.0832 | 52925.5848 | -1543.2238 | No | Yes | No |  | 3 | MAR | 15879.7402 | 4590.9847 | -7555.2653 | 649.995 | 0 | 0% | [16 empty] | 1.8 | 0.67184
[5 empty] | 2001-07-01 | 7 | 46.9 | 85449.786 | -5105.0314 | 2017-06-01 | 100000 | 20000 | 103040.6025 | -57640.9127 | 50221.9668 | -7671.8194 | No | Yes | No |  | 4 | APR | 14136.384 | 2678.7124 | -5223.3005 | 95.3369 | 0 | 0% | [16 empty] | 1.9 | 0.77137
[5 empty] | 2001-08-01 | 8 | 45.3 | 78120.9814 | -7328.8046 | 2017-07-01 | 100000 | 20000 | 97967.7582 | -72808.6742 | 44645.1727 | -19444.6123 | No | Yes | No |  | 5 | MAY | 14501.07 | 1063.7142 | -7574.0022 | -3047.8551 | -3047.8551 | 3.048% | [16 empty] | 2 | 0.87091
| Historical Storage Change Probability |  |  |  | 2001-09-01 | 9 | 45.5 | 79030.9794 | 909.998 | 2017-08-01 | 100000 | 20000 | 89806.4797 | -88335.8465 | 33246.5204 | -33552.5172 | No | Yes | No |  | 6 | JUN | 7574.0022 | -726.4523 | -6578.8295 | -2703.618 | -2703.618 | 2.704% | [16 empty] | 2.1 | 1.0202
| Extreme Drought | 10% |  |  | 2001-10-01 | 10 | 45.4 | 78575.8933 | -455.0861 | 2017-09-01 | 100000 | 20000 | 85789.6636 | -113986.5134 | 26062.1618 | -41845.5449 | No | Yes | No |  | 7 | JUL | 5223.3005 | -5072.8443 | -15167.7615 | -5576.7941 | -5576.7941 | 5.577% | [16 empty] | 2.2 | 1.269
|  | 25% |  |  | 2001-11-01 | 11 | 45.1 | 77212.7501 | -1363.1432 | 2017-10-01 | 100000 | 20000 | 84892.4946 | -126792.5251 | 21898.7011 | -51769.2933 | No | Yes | No |  | 8 | AUG | 5209.9383 | -8161.2785 | -15527.1723 | -11398.6523 | -11398.6523 | 11.4% | [16 empty] | 2.3 | 1.7169
|  | 50% |  |  | 2001-12-01 | 12 | 47 | 85911.4661 | 8698.716 | 2017-11-01 | 100000 | 20000 | 85793.0079 | -132912.4614 | 19300.2439 | -56939.2844 | No | Yes | Yes |  | 9 | SEPT | 8857.3007 | -4016.8161 | -25650.6669 | -7184.3585 | -7184.3585 | 7.184% | [16 empty] | 2.4 | 2.4137
|  | 75% |  |  | 2002-01-01 | 1 | 48 | 90554.8174 | 4643.3512 | 2017-12-01 | 100000 | 20000 | 86680.8019 | -140612.8695 | 15769.2346 | -63223.8967 | No | Yes | Yes |  | 10 | OCT | 11625.9082 | -897.169 | -12806.0117 | -4163.4607 | -4163.4607 | 4.163% | [16 empty] | 2.5 | 3.2846
| Very Wet | 95% |  |  | 2002-02-01 | 2 | 50.5 | 100000 | 9445.1826 | 2018-01-01 | 100000 | 20000 | 89765.8289 | -149900.8162 | 14805.2453 | -67956.5681 | No | Yes | Yes |  | 11 | NOV | 18232.98 | 900.5133 | -6119.9363 | -2598.4573 | -2598.4573 | 2.598% | [16 empty] | 2.6 | 4.3048
[5 empty] | 2002-03-01 | 3 | 50.1 | 99000 | -1000 | 2018-02-01 | 100000 | 20000 | 93725.6528 | -158560.6649 | 14805.2453 | -72790.1304 | No | Yes | Yes |  | 12 | DEC | 12671.071 | 887.794 | -7700.4081 | -3531.0093 | -3531.0093 | 3.531% | [16 empty] | 2.7 | 5.4992
[5 empty] | 2002-04-01 | 4 | 50.1 | 100000 | 1000 | 2018-03-01 | 100000 | 20000 | 98316.6375 | -166115.9301 | 14805.2453 | -76170.1692 | No | Yes | Yes |  | For drought fit, values in blue cells are set at 30th percentile; values in green cells modified as described below. | [23 empty] | 2.8 | 6.818
[5 empty] | 2002-05-01 | 5 | 49.6 | 98091.6692 | -1908.3308 | 2018-04-01 | 100000 | 20000 | 100995.3499 | -171339.2306 | 14805.2453 | -79608.2204 | No | Yes | Yes | [25 empty] | 2.9 | 8.2861
[5 empty] | 2002-06-01 | 6 | 50.1 | 100000 | 1908.3308 | 2018-05-01 | 100000 | 20000 | 102059.0641 | -178913.2328 | 11757.3903 | -86509.1062 | No | Yes | Yes |  | Explanation of Drought Fit |  |  | Months Affected: | [20 empty] | 3 | 9.9035
[5 empty] | 2002-07-01 | 7 | 49.3 | 96667.2639 | -3332.7361 | 2018-06-01 | 100000 | 20000 | 101332.6117 | -185492.0623 | 9053.7723 | -92637.7018 | No | Yes | Yes |  | Reason for Change: |  |  |  | Modified Value Based On: | [19 empty] | 3.1 | 11.6702
[5 empty] | 2002-08-01 | 8 | 46.7 | 88810 | -7857.2639 | 2018-07-01 | 100000 | 20000 | 96259.7674 | -200659.8238 | 3476.9782 | -104410.4947 | No | Yes | Yes |  | Value is > 0 |  |  | Feb-Apr | Assumed to be zero | [19 empty] | 3.2 | 13.5613
[5 empty] | 2002-09-01 | 9 | 46.9 | 85449.786 | -3360.214 | 2018-08-01 | 100000 | 20000 | 88098.4889 | -216186.9961 | -7921.6741 | -118518.3995 | No | Yes | Yes | [25 empty] | 3.3 | 15.6266
[5 empty] | 2002-10-01 | 10 | 47.1 | 86373.5692 | 923.7832 | 2018-09-01 | 100000 | 20000 | 84081.6728 | -241837.663 | -15106.0326 | -126811.4273 | No | Yes | Yes | [25 empty] | 3.4 | 17.8411
[5 empty] | 2002-11-01 | 11 | 47.1 | 86373.5692 | 0 | 2018-10-01 | 100000 | 20000 | 83184.5038 | -254643.6747 | -19269.4934 | -136735.1757 | No | Yes | Yes | [25 empty] | 3.5 | 20.2299
[5 empty] | 2002-12-01 | 12 | 49.8 | 99044.6402 | 12671.071 | 2018-11-01 | 100000 | 20000 | 84085.0171 | -260763.611 | -21867.9506 | -141905.1667 | No | Yes | Yes | [25 empty] | 3.6 | 22.768
[5 empty] | 2003-01-01 | 1 | 48.7 | 93834.7019 | -5209.9383 | 2018-12-01 | 100000 | 20000 | 84972.8111 | -268464.0191 | -25398.9599 | -148189.779 | No | Yes | Yes | [25 empty] | 3.7 | 25.5051
[5 empty] | 2003-02-01 | 2 | 49.1 | 95720.6629 | 1885.961 | 2019-01-01 | 100000 | 20000 | 88057.8382 | -277751.9658 | -26362.9491 | -152922.4505 | No | Yes | Yes | [25 empty] | 3.8 | 28.4164
[5 empty] | 2003-03-01 | 3 | 49.4 | 97141.6343 | 1420.9714 | 2019-02-01 | 100000 | 20000 | 92017.662 | -286411.8145 | -26362.9491 | -157756.0127 | No | Yes | Yes | [25 empty] | 3.9 | 31.5019
[5 empty] | 2003-04-01 | 4 | 50 | 100000 | 2858.3657 | 2019-03-01 | 100000 | 20000 | 96608.6467 | -293967.0797 | -26362.9491 | -161136.0516 | No | Yes | Yes | [25 empty] | 4 | 34.7865
[5 empty] | 2003-05-01 | 5 | 48.4 | 92425.9978 | -7574.0022 | 2019-04-01 | 100000 | 20000 | 99287.3591 | -299190.3802 | -26362.9491 | -164574.1027 | No | Yes | Yes | [25 empty] | 4.1 | 38.2452
[5 empty] | 2003-06-01 | 6 | 50.8 | 100000 | 7574.0022 | 2019-05-01 | 100000 | 20000 | 100351.0733 | -306764.3824 | -29410.8042 | -171474.9886 | No | Yes | Yes | [25 empty] | 4.2 | 41.8782
[5 empty] | 2003-07-01 | 7 | 49.4 | 97141.6343 | -2858.3657 | 2019-06-01 | 100000 | 20000 | 99624.6209 | -313343.2119 | -32114.4222 | -177603.5842 | No | Yes | Yes | [25 empty] | 4.3 | 45.6853
[5 empty] | 2003-08-01 | 8 | 45 | 84100 | -13041.6343 | 2019-07-01 | 100000 | 20000 | 94551.7766 | -328510.9734 | -37691.2163 | -189376.377 | No | Yes | Yes | [25 empty] | 4.4 | 49.6915
[5 empty] | 2003-09-01 | 9 | 44.9 | 76306.5841 | -7793.4159 | 2019-08-01 | 100000 | 20000 | 86390.4981 | -344038.1457 | -49089.8686 | -203484.2819 | No | Yes | Yes | [25 empty] | 4.5 | 53.8967
[5 empty] | 2003-10-01 | 10 | 45.5 | 79030.9794 | 2724.3953 | 2019-09-01 | 100000 | 20000 | 82373.682 | -369688.8126 | -56274.2271 | -211777.3096 | No | Yes | Yes | [25 empty] | 4.6 | 58.3259
[5 empty] | 2003-11-01 | 11 | 46.7 | 84527.5207 | 5496.5413 | 2019-10-01 | 100000 | 20000 | 81476.5131 | -382494.8243 | -60437.6879 | -221701.058 | No | Yes | Yes | [25 empty] | 4.7 | 62.9541
[5 empty] | 2003-12-01 | 12 | 46 | 81313.5015 | -3214.0191 | 2019-11-01 | 100000 | 20000 | 82377.0263 | -388614.7606 | -63036.1451 | -226871.0491 | No | Yes | Yes | [25 empty] | 4.8 | 67.8312
[5 empty] | 2004-01-01 | 1 | 47.7 | 89156.8379 | 7843.3363 | [35 empty] | 4.9 | 72.982
[5 empty] | 2004-02-01 | 2 | 48.4 | 92425.9978 | 3269.1599 | [35 empty] | 5 | 78.4314
[5 empty] | 2004-03-01 | 3 | 50.5 | 97100 | 4674.0022 | [35 empty] | 5.1 | 84.1545
[5 empty] | 2004-04-01 | 4 | 49.3 | 96667.2639 | -432.7361 | [35 empty] | 5.2 | 90.2011
Notes: |  |  |  |  | 2004-05-01 | 5 | 50.1 | 100000 | 3332.7361 | [35 empty] | 5.3 | 96.5462
[5 empty] | 2004-06-01 | 6 | 50 | 100000 | 0 | [35 empty] | 5.4 | 103.1651
[5 empty] | 2004-07-01 | 7 | 48.7 | 93834.7019 | -6165.2981 | [35 empty] | 5.5 | 110.0577
[5 empty] | 2004-08-01 | 8 | 49.8 | 99044.6402 | 5209.9383 | [35 empty] | 5.6 | 117.2738
[5 empty] | 2004-09-01 | 9 | 49.2 | 96193.8141 | -2850.8261 | [35 empty] | 5.7 | 124.7885
[5 empty] | 2004-10-01 | 10 | 47.7 | 89156.8379 | -7036.9762 | [35 empty] | 5.8 | 132.6018
[5 empty] | 2004-11-01 | 11 | 49.8 | 99044.6402 | 9887.8023 | [35 empty] | 5.9 | 140.7385
[5 empty] | 2004-12-01 | 12 | 50.1 | 100000 | 955.3598 | [35 empty] | 6 | 149.1988
[5 empty] | 2005-01-01 | 1 | 49.7 | 98567.9556 | -1432.0444 | [35 empty] | 6.1 | 158.0322
[5 empty] | 2005-02-01 | 2 | 49.4 | 97141.6343 | -1426.3213 | [35 empty] | 6.2 | 167.3385
[5 empty] | 2005-03-01 | 3 | 50.4 | 100000 | 2858.3657 | [35 empty] | 6.3 | 177.0927
[5 empty] | 2005-04-01 | 4 | 48.9 | 94776.6995 | -5223.3005 | [35 empty] | 6.4 | 187.2698
[5 empty] | 2005-05-01 | 5 | 48.9 | 94776.6995 | 0 | [35 empty] | 6.5 | 197.87
[5 empty] | 2005-06-01 | 6 | 48.5 | 92894.9438 | -1881.7557 | [35 empty] | 6.6 | 208.8932
[5 empty] | 2005-07-01 | 7 | 47.6 | 88691.6492 | -4203.2945 | [35 empty] | 6.7 | 220.3394
[5 empty] | 2005-08-01 | 8 | 45.5 | 79030.9794 | -9660.6699 | [35 empty] | 6.8 | 232.1589
[5 empty] | 2005-09-01 | 9 | 43.8 | 71356.8478 | -7674.1316 | [35 empty] | 6.9 | 244.4262
[5 empty] | 2005-10-01 | 10 | 41 | 66100 | -5256.8478 | [35 empty] | 7 | 257.0917
[5 empty] | 2005-11-01 | 11 | 41.2 | 60112.123 | -5987.877 | [35 empty] | 7.1 | 270.205
[5 empty] | 2005-12-01 | 12 | 39.5 | 53449.5869 | -6662.5361 | [35 empty] | 7.2 | 283.7165
[5 empty] | 2006-01-01 | 1 | 40.8 | 58487.4589 | 5037.872 | [35 empty] | 7.3 | 297.7008
[5 empty] | 2006-02-01 | 2 | 43.9 | 71804.1206 | 13316.6617 | [35 empty] | 7.4 | 312.133
[5 empty] | 2006-03-01 | 3 | 48.1 | 87100 | 15295.8794 | [35 empty] | 7.5 | 327.0628
[5 empty] | 2006-04-01 | 4 | 49.5 | 97616.3283 | 10516.3283 | [35 empty] | 7.6 | 342.4903
[5 empty] | 2006-05-01 | 5 | 48.1 | 91021.698 | -6594.6302 | [35 empty] | 7.7 | 358.4154
[5 empty] | 2006-06-01 | 6 | 47.5 | 88227.2071 | -2794.4909 | [35 empty] | 7.8 | 374.8631
[5 empty] | 2006-07-01 | 7 | 46.6 | 84066.8856 | -4160.3215 | [35 empty] | 7.9 | 391.8583
[5 empty] | 2006-08-01 | 8 | 41.3 | 72100 | -11966.8856 | [35 empty] | 8 | 409.3759
[5 empty] | 2006-09-01 | 9 | 42 | 63473.8977 | -8626.1023 | [35 empty] | 8.1 | 427.3664
[5 empty] | 2006-10-01 | 10 | 41.8 | 62623.2706 | -850.6271 | [35 empty] | 8.2 | 445.8545
[5 empty] | 2006-11-01 | 11 | 45.9 | 80856.2506 | 18232.98 | [35 empty] | 8.3 | 464.7905
[5 empty] | 2006-12-01 | 12 | 46.9 | 85449.786 | 4593.5354 | [35 empty] | 8.4 | 484.2241
[5 empty] | 2007-01-01 | 1 | 50.8 | 100000 | 14550.214 | [35 empty] | 8.5 | 504.2301
[5 empty] | 2007-02-01 | 2 | 48.5 | 92894.9438 | -7105.0562 | [35 empty] | 8.6 | 524.8333
[5 empty] | 2007-03-01 | 3 | 49.5 | 97616.3283 | 4721.3845 | [35 empty] | 8.7 | 546.0336
[5 empty] | 2007-04-01 | 4 | 49.7 | 98567.9556 | 951.6274 | [35 empty] | 8.8 | 567.881
[5 empty] | 2007-05-01 | 5 | 49.4 | 97141.6343 | -1426.3213 | [35 empty] | 8.9 | 590.3504
[5 empty] | 2007-06-01 | 6 | 51.4 | 100000 | 2858.3657 | [35 empty] | 9 | 613.5662
[5 empty] | 2007-07-01 | 7 | 51.5 | 100000 | 0 | [35 empty] | 9.1 | 637.5286
[5 empty] | 2007-08-01 | 8 | 50 | 100000 | 0 | [35 empty] | 9.2 | 662.3121
[5 empty] | 2007-09-01 | 9 | 49.6 | 98091.6692 | -1908.3308 | [35 empty] | 9.3 | 687.8421
[5 empty] | 2007-10-01 | 10 | 47.8 | 93100 | -4991.6692 | [35 empty] | 9.4 | 714.1186
[5 empty] | 2007-11-01 | 11 | 47.7 | 89156.8379 | -3943.1621 | [35 empty] | 9.5 | 741.0172
[5 empty] | 2007-12-01 | 12 | 48.5 | 92894.9438 | 3738.1059 | [35 empty] | 9.6 | 768.513
[5 empty] | 2008-01-01 | 1 | 46.5 | 83606.9971 | -9287.9467 | [35 empty] | 9.7 | 796.606
[5 empty] | 2008-02-01 | 2 | 46.3 | 82688.2154 | -918.7817 | [35 empty] | 9.8 | 825.2463
[5 empty] | 2008-03-01 | 3 | 49.7 | 98567.9556 | 15879.7402 | [35 empty] | 9.9 | 854.4342
[5 empty] | 2008-04-01 | 4 | 49.8 | 99044.6402 | 476.6846 | [35 empty] | 10 | 884.1694
[5 empty] | 2008-05-01 | 5 | 49.6 | 98091.6692 | -952.971 | [35 empty] | 10.1 | 914.4023
[5 empty] | 2008-06-01 | 6 | 48.3 | 91957.3007 | -6134.3685 | [35 empty] | 10.2 | 945.2324
[5 empty] | 2008-07-01 | 7 | 47.4 | 87763.2378 | -4194.0629 | [35 empty] | 10.3 | 976.6099
[5 empty] | 2008-08-01 | 8 | 44.7 | 79200 | -8563.2378 | [35 empty] | 10.4 | 1008.6095
[5 empty] | 2008-09-01 | 9 | 44.8 | 75853.9365 | -3346.0635 | [35 empty] | 10.5 | 1041.281
[5 empty] | 2008-10-01 | 10 | 41.9 | 63047.9248 | -12806.0117 | [35 empty] | 10.6 | 1074.6491
[5 empty] | 2008-11-01 | 11 | 41.8 | 62623.2706 | -424.6541 | [35 empty] | 10.7 | 1108.6643
[5 empty] | 2008-12-01 | 12 | 43 | 67808.5249 | 5185.2543 | [35 empty] | 10.8 | 1143.3264
[5 empty] | 2009-01-01 | 1 | 43.5 | 70019.8816 | 2211.3566 | [35 empty] | 10.9 | 1178.6354
[5 empty] | 2009-02-01 | 2 | 41.5 | 61360.0328 | -8659.8487 | [35 empty] | 11 | 1214.6163
[5 empty] | 2009-03-01 | 3 | 44.3 | 73598.6115 | 12238.5787 | [35 empty] | 11.1 | 1251.2939
[5 empty] | 2009-04-01 | 4 | 47.7 | 84100 | 10501.3885 | [35 empty] | 11.2 | 1288.6185
[5 empty] | 2009-05-01 | 5 | 50.5 | 96000 | 11900 | [35 empty] | 11.3 | 1326.5651
[5 empty] | 2009-06-01 | 6 | 50.4 | 100000 | 4000 | [35 empty] | 11.4 | 1365.1836
[5 empty] | 2009-07-01 | 7 | 47.5 | 88227.2071 | -11772.7929 | [35 empty] | 11.5 | 1404.4491
[5 empty] | 2009-08-01 | 8 | 46 | 83100 | -5127.2071 | [35 empty] | 11.6 | 1444.4362
[5 empty] | 2009-09-01 | 9 | 48.3 | 91957.3007 | 8857.3007 | [35 empty] | 11.7 | 1485.1199
[5 empty] | 2009-10-01 | 10 | 50.2 | 100000 | 8042.6993 | [35 empty] | 11.8 | 1526.4756
[5 empty] | 2009-11-01 | 11 | 49.3 | 96667.2639 | -3332.7361 | [35 empty] | 11.9 | 1568.5528
[5 empty] | 2009-12-01 | 12 | 49.2 | 96193.8141 | -473.4498 | [35 empty] | 12 | 1611.4014
[5 empty] | 2010-01-01 | 1 | 48.5 | 92894.9438 | -3298.8703 | [35 empty] | 12.1 | 1654.9965
[5 empty] | 2010-02-01 | 2 | 49.5 | 97616.3283 | 4721.3845 | [35 empty] | 12.2 | 1699.363
[5 empty] | 2010-03-01 | 3 | 49.4 | 97141.6343 | -474.6939 | [35 empty] | 12.3 | 1744.4262
[5 empty] | 2010-04-01 | 4 | 50.3 | 100000 | 2858.3657 | [35 empty] | 12.4 | 1790.2857
[5 empty] | 2010-05-01 | 5 | 50 | 100000 | 0 | [35 empty] | 12.5 | 1836.9165
[5 empty] | 2010-06-01 | 6 | 48.9 | 94776.6995 | -5223.3005 | [35 empty] | 12.6 | 1884.2689
[5 empty] | 2010-07-01 | 7 | 50.3 | 100000 | 5223.3005 | [35 empty] | 12.7 | 1932.3181
[5 empty] | 2010-08-01 | 8 | 46.6 | 89100 | -10900 | [35 empty] | 12.8 | 1981.0391
[5 empty] | 2010-09-01 | 9 | 49.4 | 97141.6343 | 8041.6343 | [35 empty] | 12.9 | 2030.4817
[5 empty] | 2010-10-01 | 10 | 49.4 | 97141.6343 | 0 | [35 empty] | 13 | 2080.6211
[5 empty] | 2010-11-01 | 11 | 48.1 | 91021.698 | -6119.9363 | [35 empty] | 13.1 | 2131.4572
[5 empty] | 2010-12-01 | 12 | 47.1 | 86373.5692 | -4648.1288 | [35 empty] | 13.2 | 2183.0148
[5 empty] | 2011-01-01 | 1 | 49.4 | 97141.6343 | 10768.0651 | [35 empty] | 13.3 | 2235.2195
[5 empty] | 2011-02-01 | 2 | 49.8 | 99044.6402 | 1903.0059 | [35 empty] | 13.4 | 2288.1457
[5 empty] | 2011-03-01 | 3 | 48.2 | 91489.3749 | -7555.2653 | [35 empty] | 13.5 | 2341.694
[5 empty] | 2011-04-01 | 4 | 47.1 | 86373.5692 | -5115.8057 | [35 empty] | 13.6 | 2395.8893
[5 empty] | 2011-05-01 | 5 | 49.4 | 97141.6343 | 10768.0651 | [35 empty] | 13.7 | 2450.7813
[5 empty] | 2011-06-01 | 6 | 48.1 | 91021.698 | -6119.9363 | [35 empty] | 13.8 | 2506.2954
[5 empty] | 2011-07-01 | 7 | 44.8 | 75853.9365 | -15167.7615 | [35 empty] | 13.9 | 2562.4813
[5 empty] | 2011-08-01 | 8 | 42.2 | 64330.6211 | -11523.3154 | [35 empty] | 14 | 2619.3142
[5 empty] | 2011-09-01 | 9 | 40.4 | 56901.4134 | -7429.2077 | [35 empty] | 14.1 | 2676.819
[5 empty] | 2011-10-01 | 10 | 41.2 | 60112.123 | 3210.7097 | [35 empty] | 14.2 | 2734.9955
[5 empty] | 2011-11-01 | 11 | 41.8 | 62623.2706 | 2511.1476 | [35 empty] | 14.3 | 2793.8191
[5 empty] | 2011-12-01 | 12 | 43.3 | 69132.4027 | 6509.1321 | [35 empty] | 14.4 | 2853.3891
[5 empty] | 2012-01-01 | 1 | 45.2 | 77666.7662 | 8534.3635 | [35 empty] | 14.5 | 2913.7056
[5 empty] | 2012-02-01 | 2 | 45.9 | 80856.2506 | 3189.4844 | [35 empty] | 14.6 | 2974.8184
[5 empty] | 2012-03-01 | 3 | 46 | 81313.5015 | 457.2509 | [35 empty] | 14.7 | 3036.7274
[5 empty] | 2012-04-01 | 4 | 46.8 | 84988.305 | 3674.8034 | [35 empty] | 14.8 | 3099.358
[5 empty] | 2012-05-01 | 5 | 45.5 | 79030.9794 | -5957.3256 | [35 empty] | 14.9 | 3162.7849
[5 empty] | 2012-06-01 | 6 | 45.4 | 78575.8933 | -455.0861 | [35 empty] | 15 | 3226.9334
[5 empty] | 2012-07-01 | 7 | 44.7 | 75401.9857 | -3173.9076 | [35 empty] | 15.1 | 3291.9528
[5 empty] | 2012-08-01 | 8 | 43.2 | 68690.1563 | -6711.8294 | [35 empty] | 15.2 | 3357.9924
[5 empty] | 2012-09-01 | 9 | 43.7 | 70910.5703 | 2220.4141 | [35 empty] | 15.3 | 3424.8532
[5 empty] | 2012-10-01 | 10 | 43.9 | 71804.1206 | 893.5503 | [35 empty] | 15.4 | 3492.6097
[5 empty] | 2012-11-01 | 11 | 43.7 | 70910.5703 | -893.5503 | [35 empty] | 15.5 | 3561.1625
[5 empty] | 2012-12-01 | 12 | 42.4 | 65192.8436 | -5717.7267 | [35 empty] | 15.6 | 3630.5365
[5 empty] | 2013-01-01 | 1 | 43.7 | 70910.5703 | 5717.7267 | [35 empty] | 15.7 | 3700.7813
[5 empty] | 2013-02-01 | 2 | 45.2 | 77666.7662 | 6756.1959 | [35 empty] | 15.8 | 3771.7478
[5 empty] | 2013-03-01 | 3 | 44.1 | 72700.0348 | -4966.7314 | [35 empty] | 15.9 | 3843.5105
[5 empty] | 2013-04-01 | 4 | 47.2 | 86836.4188 | 14136.384 | [35 empty] | 16 | 3915.9699
[5 empty] | 2013-05-01 | 5 | 49.4 | 97141.6343 | 10305.2155 | [35 empty] | 16.1 | 3989.1261
[5 empty] | 2013-06-01 | 6 | 50 | 100000 | 2858.3657 | [35 empty] | 16.2 | 4063.0785
[5 empty] | 2013-07-01 | 7 | 47.5 | 88227.2071 | -11772.7929 | [35 empty] | 16.3 | 4137.6779
[5 empty] | 2013-08-01 | 8 | 44.1 | 72700.0348 | -15527.1723 | [35 empty] | 16.4 | 4213.0238
[5 empty] | 2013-09-01 | 9 | 42.7 | 66495.0732 | -6204.9617 | [35 empty] | 16.5 | 4289.0166
[5 empty] | 2013-10-01 | 10 | 45.3 | 78120.9814 | 11625.9082 | [35 empty] | 16.6 | 4365.6813
[5 empty] | 2013-11-01 | 11 | 45 | 76759.4307 | -1361.5507 | [35 empty] | 16.7 | 4443.0427
[5 empty] | 2013-12-01 | 12 | 44.2 | 73149.1739 | -3610.2568 | [35 empty] | 16.8 | 4521.0511
[5 empty] | 2014-01-01 | 1 | 43.3 | 69132.4027 | -4016.7712 | [35 empty] | 16.9 | 4599.781
[5 empty] | 2014-02-01 | 2 | 44 | 72251.7667 | 3119.364 | [35 empty] | 17 | 4679.1828
[5 empty] | 2014-03-01 | 3 | 46.8 | 84988.305 | 12736.5383 | [35 empty] | 17.1 | 4759.2814
[5 empty] | 2014-04-01 | 4 | 46.6 | 84066.8856 | -921.4193 | [35 empty] | 17.2 | 4840.1264
[5 empty] | 2014-05-01 | 5 | 49.7 | 98567.9556 | 14501.07 | [35 empty] | 17.3 | 4921.6184
[5 empty] | 2014-06-01 | 6 | 50.5 | 100000 | 1432.0444 | [35 empty] | 17.4 | 5003.9564
[5 empty] | 2014-07-01 | 7 | 48.8 | 94305.2653 | -5694.7347 | [35 empty] | 17.5 | 5086.9663
[5 empty] | 2014-08-01 | 8 | 45.6 | 79486.5134 | -14818.7519 | [35 empty] | 17.6 | 5170.7226
[5 empty] | 2014-09-01 | 9 | 44.4 | 74048.8454 | -5437.668 | [35 empty] | 17.7 | 5255.325
[5 empty] | 2014-10-01 | 10 | 41.7 | 62200.5823 | -11848.2632 | [35 empty] | 17.8 | 5340.7236
[5 empty] | 2014-11-01 | 11 | 41 | 59293.2965 | -2907.2858 | [35 empty] | 17.9 | 5427.0678
[5 empty] | 2014-12-01 | 12 | 39 | 51592.8884 | -7700.4081 | [35 empty] | 18 | 5514.2331
[5 empty] | 2015-01-01 | 1 | 43 | 67808.5249 | 16215.6365 | [35 empty] | 18.1 | 5602.344
[5 empty] | 2015-02-01 | 2 | 45.3 | 78120.9814 | 10312.4565 | [35 empty] | 18.2 | 5691.4502
[5 empty] | 2015-03-01 | 3 | 45.5 | 79030.9794 | 909.998 | [35 empty] | 18.3 | 5781.4273
[5 empty] | 2015-04-01 | 4 | 47 | 85911.4661 | 6880.4867 | [35 empty] | 18.4 | 5872.4246
[5 empty] | 2015-05-01 | 5 | 49.2 | 96193.8141 | 10282.348 | [35 empty] | 18.5 | 5964.2928
[5 empty] | 2015-06-01 | 6 | 53.4 | 100000 | 3806.1859 | [35 empty] | 18.6 | 6057.1315
[5 empty] | 2015-07-01 | 7 | 50.2 | 100000 | 0 | [35 empty] | 18.7 | 6150.9903
[5 empty] | 2015-08-01 | 8 | 48.9 | 94776.6995 | -5223.3005 | [35 empty] | 18.8 | 6245.7699
[5 empty] | 2015-09-01 | 9 | 45.7 | 79942.7441 | -14833.9554 | [35 empty] | 18.9 | 6341.6194
[5 empty] | 2015-10-01 | 10 | 45.1 | 77212.7501 | -2729.994 | [35 empty] | 19 | 6438.3647
[5 empty] | 2015-11-01 | 11 | 52 | 100000 | 22787.2499 | [35 empty] | 19.1 | 6536.18
[5 empty] | 2015-12-01 | 12 | 53.4 | 100000 | 0 | [35 empty] | 19.2 | 6635.2145
[5 empty] | 2016-01-01 | 1 | 49.9 | 99522.345 | -477.655 | [35 empty] | 19.3 | 6735.3936
[5 empty] | 2016-02-01 | 2 | 49.4 | 97141.6343 | -2380.7107 | [35 empty] | 19.4 | 6836.8916
[5 empty] | 2016-03-01 | 3 |  | #N/A | #N/A | [35 empty] | 19.5 | 6939.6088
[5 empty] | 2016-04-01 | 4 |  | #N/A | #N/A | [35 empty] | 19.6 | 7043.62
[5 empty] | 2016-05-01 | 5 |  | #N/A | #N/A | [35 empty] | 19.7 | 7148.9499
[5 empty] | 2016-06-01 | 6 |  | #N/A | #N/A | [35 empty] | 19.8 | 7255.4992
[5 empty] | 2016-07-01 | 7 |  | #N/A | #N/A | [35 empty] | 19.9 | 7363.3921
[5 empty] | 2016-08-01 | 8 |  | #N/A | #N/A | [35 empty] | 20 | 7472.5291
[5 empty] | 2016-09-01 | 9 |  | #N/A | #N/A | [35 empty] | 20.1 | 7583.1094
[5 empty] | 2016-10-01 | 10 |  | #N/A | #N/A | [35 empty] | 20.2 | 7695.1826
[5 empty] | 2016-11-01 | 11 |  | #N/A | #N/A | [35 empty] | 20.3 | 7808.724
[5 empty] | 2016-12-01 | 12 |  | #N/A | #N/A | [35 empty] | 20.4 | 7923.8828
[45 empty] | 20.5 | 8040.6589
[45 empty] | 20.6 | 8159.2515
[45 empty] | 20.7 | 8279.9343
[45 empty] | 20.8 | 8402.5829
[45 empty] | 20.9 | 8527.2718
[45 empty] | 21 | 8653.7026
[45 empty] | 21.1 | 8781.7757
[45 empty] | 21.2 | 8911.5905
[45 empty] | 21.3 | 9042.8237
[45 empty] | 21.4 | 9175.5499
[45 empty] | 21.5 | 9309.6944
[45 empty] | 21.6 | 9445.2573
[45 empty] | 21.7 | 9582.1887
[45 empty] | 21.8 | 9720.3394
[45 empty] | 21.9 | 9859.8835
[45 empty] | 22 | 10000.6967
[45 empty] | 22.1 | 10142.7789
[45 empty] | 22.2 | 10286.1551
[45 empty] | 22.3 | 10430.7256
[45 empty] | 22.4 | 10576.6896
[45 empty] | 22.5 | 10723.8479
[45 empty] | 22.6 | 10872.3251
[45 empty] | 22.7 | 11022.2206
[45 empty] | 22.8 | 11173.3851
[45 empty] | 22.9 | 11325.968
[45 empty] | 23 | 11479.7701
[45 empty] | 23.1 | 11634.7915
[45 empty] | 23.2 | 11791.1317
[45 empty] | 23.3 | 11948.6414
[45 empty] | 23.4 | 12107.5197
[45 empty] | 23.5 | 12267.667
[45 empty] | 23.6 | 12429.2077
[45 empty] | 23.7 | 12592.3161
[45 empty] | 23.8 | 12756.6687
[45 empty] | 23.9 | 12922.3898
[45 empty] | 24 | 13089.2306
[45 empty] | 24.1 | 13257.1663
[45 empty] | 24.2 | 13426.1969
[45 empty] | 24.3 | 13596.1232
[45 empty] | 24.4 | 13767.0947
[45 empty] | 24.5 | 13938.8872
[45 empty] | 24.6 | 14111.6005
[45 empty] | 24.7 | 14285.3837
[45 empty] | 24.8 | 14460.0378
[45 empty] | 24.9 | 14635.8615
[45 empty] | 25 | 14812.8048
[45 empty] | 25.1 | 14991.0421
[45 empty] | 25.2 | 15170.6231
[45 empty] | 25.3 | 15351.274
[45 empty] | 25.4 | 15533.2189
[45 empty] | 25.5 | 15716.1839
[45 empty] | 25.6 | 15900.3434
[45 empty] | 25.7 | 16085.7221
[45 empty] | 25.8 | 16272.121
[45 empty] | 25.9 | 16459.789
[45 empty] | 26 | 16648.502
[45 empty] | 26.1 | 16838.3099
[45 empty] | 26.2 | 17029.3122
[45 empty] | 26.3 | 17221.2352
[45 empty] | 26.4 | 17414.3277
[45 empty] | 26.5 | 17608.3159
[45 empty] | 26.6 | 17803.2995
[45 empty] | 26.7 | 17999.4775
[45 empty] | 26.8 | 18196.5761
[45 empty] | 26.9 | 18394.8691
[45 empty] | 27 | 18594.1077
[45 empty] | 27.1 | 18794.4162
[45 empty] | 27.2 | 18995.9192
[45 empty] | 27.3 | 19198.3677
[45 empty] | 27.4 | 19402.0106
[45 empty] | 27.5 | 19606.5741
[45 empty] | 27.6 | 19812.1827
[45 empty] | 27.7 | 20019.0106
[45 empty] | 27.8 | 20226.7592
[45 empty] | 27.9 | 20435.5778
[45 empty] | 28 | 20645.2424
[45 empty] | 28.1 | 20855.9769
[45 empty] | 28.2 | 21067.8561
[45 empty] | 28.3 | 21280.6062
[45 empty] | 28.4 | 21494.476
[45 empty] | 28.5 | 21709.1918
[45 empty] | 28.6 | 21924.8532
[45 empty] | 28.7 | 22141.6343
[45 empty] | 28.8 | 22359.2615
[45 empty] | 28.9 | 22578.0332
[45 empty] | 29 | 22797.6759
[45 empty] | 29.1 | 23018.3388
[45 empty] | 29.2 | 23240.1961
[45 empty] | 29.3 | 23462.974
[45 empty] | 29.4 | 23686.9215
[45 empty] | 29.5 | 23911.7896
[45 empty] | 29.6 | 24137.7277
[45 empty] | 29.7 | 24364.885
[45 empty] | 29.8 | 24592.9631
[45 empty] | 29.9 | 24822.2106
[45 empty] | 30 | 25052.4535
[45 empty] | 30.1 | 25284.04
[45 empty] | 30.2 | 25516.9951
[45 empty] | 30.3 | 25750.9953
[45 empty] | 30.4 | 25986.3143
[45 empty] | 30.5 | 26222.6784
[45 empty] | 30.6 | 26460.1871
[45 empty] | 30.7 | 26698.9897
[45 empty] | 30.8 | 26938.8375
[45 empty] | 30.9 | 27180.0786
[45 empty] | 31 | 27422.4147
[45 empty] | 31.1 | 27666.0446
[45 empty] | 31.2 | 27911.1177
[45 empty] | 31.3 | 28157.2609
[45 empty] | 31.4 | 28404.7726
[45 empty] | 31.5 | 28653.3294
[45 empty] | 31.6 | 28903.1054
[45 empty] | 31.7 | 29154.2998
[45 empty] | 31.8 | 29406.5641
[45 empty] | 31.9 | 29660.3215
[45 empty] | 32 | 29915.5469
[45 empty] | 32.1 | 30172.3151
[45 empty] | 32.2 | 30430.8251
[45 empty] | 32.3 | 30690.8032
[45 empty] | 32.4 | 30952.5978
[45 empty] | 32.5 | 31215.8605
[45 empty] | 32.6 | 31480.7903
[45 empty] | 32.7 | 31747.4619
[45 empty] | 32.8 | 32015.6017
[45 empty] | 32.9 | 32285.5579
[45 empty] | 33 | 32556.9573
[45 empty] | 33.1 | 32829.8746
[45 empty] | 33.2 | 33104.5337
[45 empty] | 33.3 | 33380.6858
[45 empty] | 33.4 | 33658.7539
[45 empty] | 33.5 | 33938.3398
[45 empty] | 33.6 | 34219.4934
[45 empty] | 33.7 | 34502.339
[45 empty] | 33.8 | 34786.4786
[45 empty] | 33.9 | 35072.2106
[45 empty] | 34 | 35359.0873
[45 empty] | 34.1 | 35647.3077
[45 empty] | 34.2 | 35936.9712
[45 empty] | 34.3 | 36227.7297
[45 empty] | 34.4 | 36519.9811
[45 empty] | 34.5 | 36813.3274
[45 empty] | 34.6 | 37108.0422
[45 empty] | 34.7 | 37404.2998
[45 empty] | 34.8 | 37701.8015
[45 empty] | 34.9 | 38000.8211
[45 empty] | 35 | 38300.9107
[45 empty] | 35.1 | 38602.2445
[45 empty] | 35.2 | 38905.0463
[45 empty] | 35.3 | 39208.943
[45 empty] | 35.4 | 39514.3326
[45 empty] | 35.5 | 39820.8669
[45 empty] | 35.6 | 40128.7698
[45 empty] | 35.7 | 40438.2403
[45 empty] | 35.8 | 40749.0047
[45 empty] | 35.9 | 41061.4114
[45 empty] | 36 | 41375.0871
[45 empty] | 36.1 | 41690.2807
[45 empty] | 36.2 | 42007.2161
[45 empty] | 36.3 | 42325.5698
[45 empty] | 36.4 | 42645.74
[45 empty] | 36.5 | 42967.3286
[45 empty] | 36.6 | 43290.5096
[45 empty] | 36.7 | 43615.6066
[45 empty] | 36.8 | 43942.2713
[45 empty] | 36.9 | 44270.852
[45 empty] | 37 | 44601.0003
[45 empty] | 37.1 | 44932.9899
[45 empty] | 37.2 | 45266.9454
[45 empty] | 37.3 | 45602.4435
[45 empty] | 37.4 | 45939.9323
[45 empty] | 37.5 | 46279.1132
[45 empty] | 37.6 | 46620.1354
[45 empty] | 37.7 | 46963.2726
[45 empty] | 37.8 | 47308.1268
[45 empty] | 37.9 | 47655.096
[45 empty] | 38 | 48003.7822
[45 empty] | 38.1 | 48354.4093
[45 empty] | 38.2 | 48707.1016
[45 empty] | 38.3 | 49061.4611
[45 empty] | 38.4 | 49417.9357
[45 empty] | 38.5 | 49776.0526
[45 empty] | 38.6 | 50135.9859
[45 empty] | 38.7 | 50497.8352
[45 empty] | 38.8 | 50861.1526
[45 empty] | 38.9 | 51226.3362
[45 empty] | 39 | 51592.8884
[45 empty] | 39.1 | 51960.9834
[45 empty] | 39.2 | 52330.845
[45 empty] | 39.3 | 52702.1001
[45 empty] | 39.4 | 53075.1468
[45 empty] | 39.5 | 53449.5869
[45 empty] | 39.6 | 53825.6196
[45 empty] | 39.7 | 54203.5433
[45 empty] | 39.8 | 54582.9601
[45 empty] | 39.9 | 54964.6163
[45 empty] | 40 | 55347.9397
[45 empty] | 40.1 | 55733.1791
[45 empty] | 40.2 | 56120.5584
[45 empty] | 40.3 | 56509.8039
[45 empty] | 40.4 | 56901.4134
[45 empty] | 40.5 | 57294.8144
[45 empty] | 40.6 | 57690.206
[45 empty] | 40.7 | 58087.9118
[45 empty] | 40.8 | 58487.4589
[45 empty] | 40.9 | 58889.3948
[45 empty] | 41 | 59293.2965
[45 empty] | 41.1 | 59699.5621
[45 empty] | 41.2 | 60112.123
[45 empty] | 41.3 | 60526.2516
[45 empty] | 41.4 | 60942.3957
[45 empty] | 41.5 | 61360.0328
[45 empty] | 41.6 | 61779.3371
[45 empty] | 41.7 | 62200.5823
[45 empty] | 41.8 | 62623.2706
[45 empty] | 41.9 | 63047.9248
[45 empty] | 42 | 63473.8977
[45 empty] | 42.1 | 63901.3885
[45 empty] | 42.2 | 64330.6211
[45 empty] | 42.3 | 64760.9734
[45 empty] | 42.4 | 65192.8436
[45 empty] | 42.5 | 65625.6594
[45 empty] | 42.6 | 66059.5949
[45 empty] | 42.7 | 66495.0732
[45 empty] | 42.8 | 66931.6214
[45 empty] | 42.9 | 67369.6128
[45 empty] | 43 | 67808.5249
[45 empty] | 43.1 | 68248.6563
[45 empty] | 43.2 | 68690.1563
[45 empty] | 43.3 | 69132.4027
[45 empty] | 43.4 | 69575.8435
[45 empty] | 43.5 | 70019.8816
[45 empty] | 43.6 | 70464.7158
[45 empty] | 43.7 | 70910.5703
[45 empty] | 43.8 | 71356.8478
[45 empty] | 43.9 | 71804.1206
[45 empty] | 44 | 72251.7667
[45 empty] | 44.1 | 72700.0348
[45 empty] | 44.2 | 73149.1739
[45 empty] | 44.3 | 73598.6115
[45 empty] | 44.4 | 74048.8454
[45 empty] | 44.5 | 74499.3033
[45 empty] | 44.6 | 74950.2837
[45 empty] | 44.7 | 75401.9857
[45 empty] | 44.8 | 75853.9365
[45 empty] | 44.9 | 76306.5841
[45 empty] | 45 | 76759.4307
[45 empty] | 45.1 | 77212.7501
[45 empty] | 45.2 | 77666.7662
[45 empty] | 45.3 | 78120.9814
[45 empty] | 45.4 | 78575.8933
[45 empty] | 45.5 | 79030.9794
[45 empty] | 45.6 | 79486.5134
[45 empty] | 45.7 | 79942.7441
[45 empty] | 45.8 | 80399.149
[45 empty] | 45.9 | 80856.2506
[45 empty] | 46 | 81313.5015
[45 empty] | 46.1 | 81771.2252
[45 empty] | 46.2 | 82229.6457
[45 empty] | 46.3 | 82688.2154
[45 empty] | 46.4 | 83147.5316
[45 empty] | 46.5 | 83606.9971
[45 empty] | 46.6 | 84066.8856
[45 empty] | 46.7 | 84527.5207
[45 empty] | 46.8 | 84988.305
[45 empty] | 46.9 | 85449.786
[45 empty] | 47 | 85911.4661
[45 empty] | 47.1 | 86373.5692
[45 empty] | 47.2 | 86836.4188
[45 empty] | 47.3 | 87299.4675
[45 empty] | 47.4 | 87763.2378
[45 empty] | 47.5 | 88227.2071
[45 empty] | 47.6 | 88691.6492
[45 empty] | 47.7 | 89156.8379
[45 empty] | 47.8 | 89622.2504
[45 empty] | 47.9 | 90088.4344
[45 empty] | 48 | 90554.8174
[45 empty] | 48.1 | 91021.698
[45 empty] | 48.2 | 91489.3749
[45 empty] | 48.3 | 91957.3007
[45 empty] | 48.4 | 92425.9978
[45 empty] | 48.5 | 92894.9438
[45 empty] | 48.6 | 93364.4123
[45 empty] | 48.7 | 93834.7019
[45 empty] | 48.8 | 94305.2653
[45 empty] | 48.9 | 94776.6995
[45 empty] | 49 | 95248.3826
[45 empty] | 49.1 | 95720.6629
[45 empty] | 49.2 | 96193.8141
[45 empty] | 49.3 | 96667.2639
[45 empty] | 49.4 | 97141.6343
[45 empty] | 49.5 | 97616.3283
[45 empty] | 49.6 | 98091.6692
[45 empty] | 49.7 | 98567.9556
[45 empty] | 49.8 | 99044.6402
[45 empty] | 49.9 | 99522.345
[45 empty] | 50 | 100000
Formulas:
Reservoir Storage Predictions = DATE(YEAR([Reservoir Storage Predictions, row below]),MONTH([Reservoir Storage Predictions, row below])-1,DAY([Reservoir Storage Predictions, row below]))
Reservoir Storage Predictions = DATE(YEAR([Reservoir Storage Predictions, row above]),MONTH([Reservoir Storage Predictions, row above])+1,DAY([Reservoir Storage Predictions, row above]))
Historical Data = DATE(YEAR([Historical Data, row above]),MONTH([Historical Data, row above])+1,DAY([Historical Data, row above]))
Access the reservoir elevation from the appropriate source. Record the level (in feet) for the first of the month and input it into the relevant box in column Y
Lookup table for storage volume. This table should not be altered except if there is a change in the bathymetry of the lake.
This table calculates statistics based on historical monthly changes in storage for the reservoir.
The drought fit (column AX) is based on the 30th percentile, with modifications as necessary (e.g., to remove anomolies or values > 0) described in the table below.
Column AY and the chart at right provide a basic check on the reasonableness of the drought fit.
The information in the average, min, and drought fit columns are the basis for future predictions in the table at left.
Group Box 15
Choose the probability required using the relevant radio button. (low = dry, high = wet)
This is the primary output of the prediction spreadsheet, indicating the number of months before the reservoir becomes at risk. The green dot indicates the reservoir is not expected to become at risk for at least the next 18 months.
This table predicts future storage based on the most recent storage records (rows 5-7), and the profiles of montly changes estimated in the "Calculation of Drought Fit" table at right.
This table calculates percentiles based on the historical monthly changes in storage for the reservoir. These percentiles are used to calculate the "Probability Fit" based on user selections in cells R26:R30.

## Off-Channel Reservoir
[5 empty] | Estimated Storage |  |  |  |  | Reservoir Storage Predictions |  |  |  | All values are in acre-feet | Calculation of Drought Fit | [11 empty] | Lake Bathymetry
| Risk | Drought Fit |  |  | Year | Month | Elevation (ft) | Storage (Acre-ft) | Change (Acre-ft) |  | Reservoir Characteristics |  | Drought Fit Forecast |  |  |  | Evaporation Location |  | I 35 Corr. |  | Most Recent Elevation: | 69.5 |  |  |  |  | Depth (ft) | Elevation (ft) | Volume (acre-ft) | Elevation (ft)
| Months to Empty | 25 |  |  | 2014-01-01 | 1 | 69.5 | 13650 |  | Date | Full Storage | At-Risk Storage | Storage | At Risk? |  |  | Pan Evaporation Assumptions |  |  | Storage Loss from Evaporation |  | Storage Loss from Consumption |  | Drought Fit | Evaporation Location Lookup |  | 20 | 70 | 14000 | 70
| Months to At Risk | 12 |  |  | 2014-02-01 | 2 | 69.5 | 13650 | 0 | 2015-12-01 | 14000 | 7000 | 13650 | No | Month (#) | Month | East TX | I 35 Corr. | West TX | Elevation (ft) | Storage (acre-ft) | Storage (acre-ft) | Elevation (ft) | Change (acre-ft) | East TX | 1 |  | 50 | 0 | 50
[5 empty] | 2014-03-01 | 3 | 69.5 | 13650 | 0 | 2016-01-01 | 14000 | 7000 | 13650 | No | 1 | JAN | 0.21667 | 0.25 | 0.35 | 69.25 | 13440 | 13407.7399 | 69.1 |  | I 35 Corr. | 2 |  | 50.1 | 70 | 50.1
| Generators at Risk | MW | Cap Fctr | MWh (2015) | 2014-04-01 | 4 | 69.5 | 13650 | 0 | 2016-02-01 | 14000 | 7000 | 13650 | No | 2 | FEB | 0.26667 | 0.33333 | 0.41667 | 68.7667 | 13090 | 13057.7399 | 68.6 | -350 | West TX | 3 |  | 50.2 | 140 | 50.2
| Generator 2 | 300 | 10% | 262800 | 2014-05-01 | 5 | 69.5 | 13650 | 0 | 2016-03-01 | 14000 | 7000 | 13160 | No | 3 | MAR | 0.4 | 0.51667 | 0.63333 | 68.0833 | 12600 | 12567.7399 | 67.9 | -490 | Location to use | 2 |  | 50.3 | 210 | 50.3
[5 empty] | 2014-06-01 | 6 | 69.5 | 13650 | 0 | 2016-04-01 | 14000 | 7000 | 12600 | No | 4 | APR | 0.5 | 0.61667 | 0.78333 | 67.2833 | 12040 | 12007.7399 | 67.1 | -560 |  |  |  | 50.4 | 280 | 50.4
[5 empty] | 2014-07-01 | 7 | 69.5 | 13650 | 0 | 2016-05-01 | 14000 | 7000 | 11970 | No | 5 | MAY | 0.59167 | 0.7 | 0.85 | 66.4 | 11410 | 11377.7399 | 66.2 | -630 |  |  |  | 50.5 | 350 | 50.5
[5 empty] | 2014-08-01 | 8 | 69.5 | 13650 | 0 | 2016-06-01 | 14000 | 7000 | 11270 | No | 6 | JUN | 0.63333 | 0.85 | 0.96667 | 65.35 | 10710 | 10677.7399 | 65.2 | -700 |  |  |  | 50.6 | 420 | 50.6
[5 empty] | 2014-09-01 | 9 | 69.5 | 13650 | 0 | 2016-07-01 | 14000 | 7000 | 10430 | No | 7 | JUL | 0.66667 | 1 | 1.0583 | 64.2 | 9870 | 9837.7399 | 64 | -840 |  |  |  | 50.7 | 490 | 50.7
| Monthly Consump | Acre-feet | gal/MWh | MWh (2015) | 2014-10-01 | 10 | 69.5 | 13650 | 0 | 2016-08-01 | 14000 | 7000 | 9660 | No | 8 | AUG | 0.64167 | 0.93333 | 0.98333 | 63.0667 | 9100 | 9067.7399 | 62.9 | -770 |  |  |  | 50.8 | 560 | 50.8
| Gas Steam-Non-reheat | 32.2601 | 480 | 21900 | 2014-11-01 | 11 | 69.5 | 13650 | 0 | 2016-09-01 | 14000 | 7000 | 9100 | No | 9 | SEPT | 0.5 | 0.69167 | 0.75 | 62.2083 | 8540 | 8507.7399 | 62.1 | -560 |  |  |  | 50.9 | 630 | 50.9
|  |  |  | 0 | 2014-12-01 | 12 | 69.5 | 13650 | 0 | 2016-10-01 | 14000 | 7000 | 8610 | No | 10 | OCT | 0.4 | 0.525 | 0.58333 | 61.575 | 8050 | 8017.7399 | 61.4 | -490 |  |  |  | 51 | 700 | 51
|  |  |  | 0 | 2015-01-01 | 1 | 69.5 | 13650 | 0 | 2016-11-01 | 14000 | 7000 | 8260 | No | 11 | NOV | 0.26667 | 0.34167 | 0.41667 | 61.0583 | 7700 | 7667.7399 | 60.9 | -350 |  |  |  | 51.1 | 770 | 51.1
|  |  |  | 0 | 2015-02-01 | 2 | 69.5 | 13650 | 0 | 2016-12-01 | 14000 | 7000 | 7980 | No | 12 | DEC | 0.23333 | 0.25833 | 0.33333 | 60.6417 | 7420 | 7387.7399 | 60.5 | -280 |  |  |  | 51.2 | 840 | 51.2
[5 empty] | 2015-03-01 | 3 | 69.5 | 13650 | 0 | 2017-01-01 | 14000 | 7000 | 7700 | No | 1 | JAN | 0.21667 | 0.25 | 0.35 | 60.25 | 7140 | 7107.7399 | 60.1 | -280 |  |  |  | 51.3 | 910 | 51.3
| Reservoir Details |  |  |  | 2015-04-01 | 4 | 69.5 | 13650 | 0 | 2017-02-01 | 14000 | 7000 | 7350 | No | 2 | FEB | 0.26667 | 0.33333 | 0.41667 | 59.7667 | 6790 | 6757.7399 | 59.6 | -350 |  |  |  | 51.4 | 980 | 51.4
| Full (Conservation) | 14000 | Acre-feet |  | 2015-05-01 | 5 | 69.5 | 13650 | 0 | 2017-03-01 | 14000 | 7000 | 6860 | Yes | [13 empty] | 51.5 | 1050 | 51.5
| At-Risk Level | 7000 | Acre-feet |  | 2015-06-01 | 6 | 69.5 | 13650 | 0 | 2017-04-01 | 14000 | 7000 | 6300 | Yes | [13 empty] | 51.6 | 1120 | 51.6
[5 empty] | 2015-07-01 | 7 | 69.5 | 13650 | 0 | 2017-05-01 | 14000 | 7000 | 5670 | Yes | [13 empty] | 51.7 | 1190 | 51.7
| At-Risk Level |  | Reasons |  | 2015-08-01 | 8 | 69.5 | 13650 | 0 | 2017-06-01 | 14000 | 7000 | 4970 | Yes | [13 empty] | 51.8 | 1260 | 51.8
| 50% | Set at default level of 50% for off channel reservoirs |  |  | 2015-09-01 | 9 | 69.5 | 13650 | 0 | 2017-07-01 | 14000 | 7000 | 4130 | Yes | [13 empty] | 51.9 | 1330 | 51.9
[5 empty] | 2015-10-01 | 10 | 69.5 | 13650 | 0 | 2017-08-01 | 14000 | 7000 | 3360 | Yes | [13 empty] | 52 | 1400 | 52
[5 empty] | 2015-11-01 | 11 | 69.5 | 13650 | 0 | 2017-09-01 | 14000 | 7000 | 2800 | Yes | [13 empty] | 52.1 | 1470 | 52.1
[5 empty] | 2015-12-01 | 12 | 69.5 | 13650 | 0 | 2017-10-01 | 14000 | 7000 | 2310 | Yes | [13 empty] | 52.2 | 1540 | 52.2
[5 empty] | 2016-01-01 | 1 | 69.5 | 13650 | 0 | 2017-11-01 | 14000 | 7000 | 1960 | Yes | [13 empty] | 52.3 | 1610 | 52.3
[5 empty] | 2016-02-01 | 2 | 69.5 | 13650 | 0 | 2017-12-01 | 14000 | 7000 | 1680 | Yes | [13 empty] | 52.4 | 1680 | 52.4
[5 empty] | 2016-03-01 | 3 |  | #N/A | #N/A | 2018-01-01 | 14000 | 7000 | 1400 | Yes | [13 empty] | 52.5 | 1750 | 52.5
[5 empty] | 2016-04-01 | 4 |  | #N/A | #N/A | 2018-02-01 | 14000 | 7000 | 1050 | Yes | [13 empty] | 52.6 | 1820 | 52.6
[5 empty] | 2016-05-01 | 5 |  | #N/A | #N/A | 2018-03-01 | 14000 | 7000 | 560 | Yes | [13 empty] | 52.7 | 1890 | 52.7
[5 empty] | 2016-06-01 | 6 |  | #N/A | #N/A | 2018-04-01 | 14000 | 7000 | 0 | Yes | [13 empty] | 52.8 | 1960 | 52.8
[5 empty] | 2016-07-01 | 7 |  | #N/A | #N/A | 2018-05-01 | 14000 | 7000 | -630 | Yes | [13 empty] | 52.9 | 2030 | 52.9
[5 empty] | 2016-08-01 | 8 |  | #N/A | #N/A | 2018-06-01 | 14000 | 7000 | -1330 | Yes | [13 empty] | 53 | 2100 | 53
[5 empty] | 2016-09-01 | 9 |  | #N/A | #N/A | 2018-07-01 | 14000 | 7000 | -2170 | Yes | [13 empty] | 53.1 | 2170 | 53.1
[5 empty] | 2016-10-01 | 10 |  | #N/A | #N/A | 2018-08-01 | 14000 | 7000 | -2940 | Yes | [13 empty] | 53.2 | 2240 | 53.2
[5 empty] | 2016-11-01 | 11 |  | #N/A | #N/A | 2018-09-01 | 14000 | 7000 | -3500 | Yes | [13 empty] | 53.3 | 2310 | 53.3
[5 empty] | 2016-12-01 | 12 |  | #N/A | #N/A | 2018-10-01 | 14000 | 7000 | -3990 | Yes | [13 empty] | 53.4 | 2380 | 53.4
[10 empty] | 2018-11-01 | 14000 | 7000 | -4340 | Yes | [13 empty] | 53.5 | 2450 | 53.5
[10 empty] | 2018-12-01 | 14000 | 7000 | -4620 | Yes | [13 empty] | 53.6 | 2520 | 53.6
[10 empty] | 2019-01-01 | 14000 | 7000 | -4900 | Yes | [13 empty] | 53.7 | 2590 | 53.7
[10 empty] | 2019-02-01 | 14000 | 7000 | -5250 | Yes | [13 empty] | 53.8 | 2660 | 53.8
[10 empty] | 2019-03-01 | 14000 | 7000 | -5740 | Yes | [13 empty] | 53.9 | 2730 | 53.9
[10 empty] | 2019-04-01 | 14000 | 7000 | -6300 | Yes | [13 empty] | 54 | 2800 | 54
[10 empty] | 2019-05-01 | 14000 | 7000 | -6930 | Yes | [13 empty] | 54.1 | 2870 | 54.1
[10 empty] | 2019-06-01 | 14000 | 7000 | -7630 | Yes | [13 empty] | 54.2 | 2940 | 54.2
[10 empty] | 2019-07-01 | 14000 | 7000 | -8470 | Yes | [13 empty] | 54.3 | 3010 | 54.3
[10 empty] | 2019-08-01 | 14000 | 7000 | -9240 | Yes | [13 empty] | 54.4 | 3080 | 54.4
[10 empty] | 2019-09-01 | 14000 | 7000 | -9800 | Yes | [13 empty] | 54.5 | 3150 | 54.5
[10 empty] | 2019-10-01 | 14000 | 7000 | -10290 | Yes | [13 empty] | 54.6 | 3220 | 54.6
[10 empty] | 2019-11-01 | 14000 | 7000 | -10640 | Yes | [13 empty] | 54.7 | 3290 | 54.7
[28 empty] | 54.8 | 3360 | 54.8
[28 empty] | 54.9 | 3430 | 54.9
[28 empty] | 55 | 3500 | 55
Notes: | [27 empty] | 55.1 | 3570 | 55.1
[28 empty] | 55.2 | 3640 | 55.2
[28 empty] | 55.3 | 3710 | 55.3
[28 empty] | 55.4 | 3780 | 55.4
[28 empty] | 55.5 | 3850 | 55.5
[28 empty] | 55.6 | 3920 | 55.6
[28 empty] | 55.7 | 3990 | 55.7
[28 empty] | 55.8 | 4060 | 55.8
[28 empty] | 55.9 | 4130 | 55.9
[28 empty] | 56 | 4200 | 56
[28 empty] | 56.1 | 4270 | 56.1
[28 empty] | 56.2 | 4340 | 56.2
[28 empty] | 56.3 | 4410 | 56.3
[28 empty] | 56.4 | 4480 | 56.4
[28 empty] | 56.5 | 4550 | 56.5
[28 empty] | 56.6 | 4620 | 56.6
[28 empty] | 56.7 | 4690 | 56.7
[28 empty] | 56.8 | 4760 | 56.8
[28 empty] | 56.9 | 4830 | 56.9
[28 empty] | 57 | 4900 | 57
[28 empty] | 57.1 | 4970 | 57.1
[28 empty] | 57.2 | 5040 | 57.2
[28 empty] | 57.3 | 5110 | 57.3
[28 empty] | 57.4 | 5180 | 57.4
[28 empty] | 57.5 | 5250 | 57.5
[28 empty] | 57.6 | 5320 | 57.6
[28 empty] | 57.7 | 5390 | 57.7
[28 empty] | 57.8 | 5460 | 57.8
[28 empty] | 57.9 | 5530 | 57.9
[28 empty] | 58 | 5600 | 58
[28 empty] | 58.1 | 5670 | 58.1
[28 empty] | 58.2 | 5740 | 58.2
[28 empty] | 58.3 | 5810 | 58.3
[28 empty] | 58.4 | 5880 | 58.4
[28 empty] | 58.5 | 5950 | 58.5
[28 empty] | 58.6 | 6020 | 58.6
[28 empty] | 58.7 | 6090 | 58.7
[28 empty] | 58.8 | 6160 | 58.8
[28 empty] | 58.9 | 6230 | 58.9
[28 empty] | 59 | 6300 | 59
[28 empty] | 59.1 | 6370 | 59.1
[28 empty] | 59.2 | 6440 | 59.2
[28 empty] | 59.3 | 6510 | 59.3
[28 empty] | 59.4 | 6580 | 59.4
[28 empty] | 59.5 | 6650 | 59.5
[28 empty] | 59.6 | 6720 | 59.6
[28 empty] | 59.7 | 6790 | 59.7
[28 empty] | 59.8 | 6860 | 59.8
[28 empty] | 59.9 | 6930 | 59.9
[28 empty] | 60 | 7000 | 60
[28 empty] | 60.1 | 7070 | 60.1
[28 empty] | 60.2 | 7140 | 60.2
[28 empty] | 60.3 | 7210 | 60.3
[28 empty] | 60.4 | 7280 | 60.4
[28 empty] | 60.5 | 7350 | 60.5
[28 empty] | 60.6 | 7420 | 60.6
[28 empty] | 60.7 | 7490 | 60.7
[28 empty] | 60.8 | 7560 | 60.8
[28 empty] | 60.9 | 7630 | 60.9
[28 empty] | 61 | 7700 | 61
[28 empty] | 61.1 | 7770 | 61.1
[28 empty] | 61.2 | 7840 | 61.2
[28 empty] | 61.3 | 7910 | 61.3
[28 empty] | 61.4 | 7980 | 61.4
[28 empty] | 61.5 | 8050 | 61.5
[28 empty] | 61.6 | 8120 | 61.6
[28 empty] | 61.7 | 8190 | 61.7
[28 empty] | 61.8 | 8260 | 61.8
[28 empty] | 61.9 | 8330 | 61.9
[28 empty] | 62 | 8400 | 62
[28 empty] | 62.1 | 8470 | 62.1
[28 empty] | 62.2 | 8540 | 62.2
[28 empty] | 62.3 | 8610 | 62.3
[28 empty] | 62.4 | 8680 | 62.4
[28 empty] | 62.5 | 8750 | 62.5
[28 empty] | 62.6 | 8820 | 62.6
[28 empty] | 62.7 | 8890 | 62.7
[28 empty] | 62.8 | 8960 | 62.8
[28 empty] | 62.9 | 9030 | 62.9
[28 empty] | 63 | 9100 | 63
[28 empty] | 63.1 | 9170 | 63.1
[28 empty] | 63.2 | 9240 | 63.2
[28 empty] | 63.3 | 9310 | 63.3
[28 empty] | 63.4 | 9380 | 63.4
[28 empty] | 63.5 | 9450 | 63.5
[28 empty] | 63.6 | 9520 | 63.6
[28 empty] | 63.7 | 9590 | 63.7
[28 empty] | 63.8 | 9660 | 63.8
[28 empty] | 63.9 | 9730 | 63.9
[28 empty] | 64 | 9800 | 64
[28 empty] | 64.1 | 9870 | 64.1
[28 empty] | 64.2 | 9940 | 64.2
[28 empty] | 64.3 | 10010 | 64.3
[28 empty] | 64.4 | 10080 | 64.4
[28 empty] | 64.5 | 10150 | 64.5
[28 empty] | 64.6 | 10220 | 64.6
[28 empty] | 64.7 | 10290 | 64.7
[28 empty] | 64.8 | 10360 | 64.8
[28 empty] | 64.9 | 10430 | 64.9
[28 empty] | 65 | 10500 | 65
[28 empty] | 65.1 | 10570 | 65.1
[28 empty] | 65.2 | 10640 | 65.2
[28 empty] | 65.3 | 10710 | 65.3
[28 empty] | 65.4 | 10780 | 65.4
[28 empty] | 65.5 | 10850 | 65.5
[28 empty] | 65.6 | 10920 | 65.6
[28 empty] | 65.7 | 10990 | 65.7
[28 empty] | 65.8 | 11060 | 65.8
[28 empty] | 65.9 | 11130 | 65.9
[28 empty] | 66 | 11200 | 66
[28 empty] | 66.1 | 11270 | 66.1
[28 empty] | 66.2 | 11340 | 66.2
[28 empty] | 66.3 | 11410 | 66.3
[28 empty] | 66.4 | 11480 | 66.4
[28 empty] | 66.5 | 11550 | 66.5
[28 empty] | 66.6 | 11620 | 66.6
[28 empty] | 66.7 | 11690 | 66.7
[28 empty] | 66.8 | 11760 | 66.8
[28 empty] | 66.9 | 11830 | 66.9
[28 empty] | 67 | 11900 | 67
[28 empty] | 67.1 | 11970 | 67.1
[28 empty] | 67.2 | 12040 | 67.2
[28 empty] | 67.3 | 12110 | 67.3
[28 empty] | 67.4 | 12180 | 67.4
[28 empty] | 67.5 | 12250 | 67.5
[28 empty] | 67.6 | 12320 | 67.6
[28 empty] | 67.7 | 12390 | 67.7
[28 empty] | 67.8 | 12460 | 67.8
[28 empty] | 67.9 | 12530 | 67.9
[28 empty] | 68 | 12600 | 68
[28 empty] | 68.1 | 12670 | 68.1
[28 empty] | 68.2 | 12740 | 68.2
[28 empty] | 68.3 | 12810 | 68.3
[28 empty] | 68.4 | 12880 | 68.4
[28 empty] | 68.5 | 12950 | 68.5
[28 empty] | 68.6 | 13020 | 68.6
[28 empty] | 68.7 | 13090 | 68.7
[28 empty] | 68.8 | 13160 | 68.8
[28 empty] | 68.9 | 13230 | 68.9
[28 empty] | 69 | 13300 | 69
[28 empty] | 69.1 | 13370 | 69.1
[28 empty] | 69.2 | 13440 | 69.2
[28 empty] | 69.3 | 13510 | 69.3
[28 empty] | 69.4 | 13580 | 69.4
[28 empty] | 69.5 | 13650 | 69.5
[28 empty] | 69.6 | 13720 | 69.6
[28 empty] | 69.7 | 13790 | 69.7
[28 empty] | 69.8 | 13860 | 69.8
[28 empty] | 69.9 | 13930 | 69.9
[28 empty] | 70 | 14000 | 70
[28 empty] | 70.1 | 14070 | 70.1
[28 empty] | 70.2 | 14140 | 70.2
[28 empty] | 70.3 | 14210 | 70.3
[28 empty] | 70.4 | 14280 | 70.4
[28 empty] | 70.5 | 14350 | 70.5
[28 empty] | 70.6 | 14420 | 70.6
[28 empty] | 70.7 | 14490 | 70.7
[28 empty] | 70.8 | 14560 | 70.8
[28 empty] | 70.9 | 14630 | 70.9
[28 empty] | 71 | 14700 | 71
[28 empty] | 71.1 | 14770 | 71.1
[28 empty] | 71.2 | 14840 | 71.2
[28 empty] | 71.3 | 14910 | 71.3
[28 empty] | 71.4 | 14980 | 71.4
[28 empty] | 71.5 | 15050 | 71.5
[28 empty] | 71.6 | 15120 | 71.6
[28 empty] | 71.7 | 15190 | 71.7
[28 empty] | 71.8 | 15260 | 71.8
[28 empty] | 71.9 | 15330 | 71.9
[28 empty] | 72 | 15400 | 72
[28 empty] | 72.1 | 15470 | 72.1
[28 empty] | 72.2 | 15540 | 72.2
[28 empty] | 72.3 | 15610 | 72.3
[28 empty] | 72.4 | 15680 | 72.4
[28 empty] | 72.5 | 15750 | 72.5
[28 empty] | 72.6 | 15820 | 72.6
[28 empty] | 72.7 | 15890 | 72.7
[28 empty] | 72.8 | 15960 | 72.8
[28 empty] | 72.9 | 16030 | 72.9
[28 empty] | 73 | 16100 | 73
[28 empty] | 73.1 | 16170 | 73.1
[28 empty] | 73.2 | 16240 | 73.2
[28 empty] | 73.3 | 16310 | 73.3
[28 empty] | 73.4 | 16380 | 73.4
[28 empty] | 73.5 | 16450 | 73.5
[28 empty] | 73.6 | 16520 | 73.6
[28 empty] | 73.7 | 16590 | 73.7
[28 empty] | 73.8 | 16660 | 73.8
[28 empty] | 73.9 | 16730 | 73.9
[28 empty] | 74 | 16800 | 74
[28 empty] | 74.1 | 16870 | 74.1
[28 empty] | 74.2 | 16940 | 74.2
[28 empty] | 74.3 | 17010 | 74.3
[28 empty] | 74.4 | 17080 | 74.4
[28 empty] | 74.5 | 17150 | 74.5
[28 empty] | 74.6 | 17220 | 74.6
[28 empty] | 74.7 | 17290 | 74.7
[28 empty] | 74.8 | 17360 | 74.8
[28 empty] | 74.9 | 17430 | 74.9
[28 empty] | 75 | 17500 | 75
[28 empty] | 75.1 | 17570 | 75.1
[28 empty] | 75.2 | 17640 | 75.2
[28 empty] | 75.3 | 17710 | 75.3
[28 empty] | 75.4 | 17780 | 75.4
[28 empty] | 75.5 | 17850 | 75.5
[28 empty] | 75.6 | 17920 | 75.6
[28 empty] | 75.7 | 17990 | 75.7
[28 empty] | 75.8 | 18060 | 75.8
[28 empty] | 75.9 | 18130 | 75.9
[28 empty] | 76 | 18200 | 76
[28 empty] | 76.1 | 18270 | 76.1
[28 empty] | 76.2 | 18340 | 76.2
[28 empty] | 76.3 | 18410 | 76.3
[28 empty] | 76.4 | 18480 | 76.4
[28 empty] | 76.5 | 18550 | 76.5
[28 empty] | 76.6 | 18620 | 76.6
[28 empty] | 76.7 | 18690 | 76.7
[28 empty] | 76.8 | 18760 | 76.8
[28 empty] | 76.9 | 18830 | 76.9
[28 empty] | 77 | 18900 | 77
[28 empty] | 77.1 | 18970 | 77.1
[28 empty] | 77.2 | 19040 | 77.2
[28 empty] | 77.3 | 19110 | 77.3
[28 empty] | 77.4 | 19180 | 77.4
[28 empty] | 77.5 | 19250 | 77.5
[28 empty] | 77.6 | 19320 | 77.6
[28 empty] | 77.7 | 19390 | 77.7
[28 empty] | 77.8 | 19460 | 77.8
[28 empty] | 77.9 | 19530 | 77.9
[28 empty] | 78 | 19600 | 78
[28 empty] | 78.1 | 19670 | 78.1
[28 empty] | 78.2 | 19740 | 78.2
[28 empty] | 78.3 | 19810 | 78.3
[28 empty] | 78.4 | 19880 | 78.4
[28 empty] | 78.5 | 19950 | 78.5
[28 empty] | 78.6 | 20020 | 78.6
[28 empty] | 78.7 | 20090 | 78.7
[28 empty] | 78.8 | 20160 | 78.8
[28 empty] | 78.9 | 20230 | 78.9
[28 empty] | 79 | 20300 | 79
[28 empty] | 79.1 | 20370 | 79.1
[28 empty] | 79.2 | 20440 | 79.2
[28 empty] | 79.3 | 20510 | 79.3
[28 empty] | 79.4 | 20580 | 79.4
[28 empty] | 79.5 | 20650 | 79.5
[28 empty] | 79.6 | 20720 | 79.6
[28 empty] | 79.7 | 20790 | 79.7
[28 empty] | 79.8 | 20860 | 79.8
[28 empty] | 79.9 | 20930 | 79.9
[28 empty] | 80 | 21000 | 80
[28 empty] | 80.1 | 21070 | 80.1
[28 empty] | 80.2 | 21140 | 80.2
[28 empty] | 80.3 | 21210 | 80.3
[28 empty] | 80.4 | 21280 | 80.4
[28 empty] | 80.5 | 21350 | 80.5
[28 empty] | 80.6 | 21420 | 80.6
[28 empty] | 80.7 | 21490 | 80.7
[28 empty] | 80.8 | 21560 | 80.8
[28 empty] | 80.9 | 21630 | 80.9
[28 empty] | 81 | 21700 | 81
[28 empty] | 81.1 | 21770 | 81.1
[28 empty] | 81.2 | 21840 | 81.2
[28 empty] | 81.3 | 21910 | 81.3
[28 empty] | 81.4 | 21980 | 81.4
[28 empty] | 81.5 | 22050 | 81.5
[28 empty] | 81.6 | 22120 | 81.6
[28 empty] | 81.7 | 22190 | 81.7
[28 empty] | 81.8 | 22260 | 81.8
[28 empty] | 81.9 | 22330 | 81.9
[28 empty] | 82 | 22400 | 82
[28 empty] | 82.1 | 22470 | 82.1
[28 empty] | 82.2 | 22540 | 82.2
[28 empty] | 82.3 | 22610 | 82.3
[28 empty] | 82.4 | 22680 | 82.4
[28 empty] | 82.5 | 22750 | 82.5
[28 empty] | 82.6 | 22820 | 82.6
[28 empty] | 82.7 | 22890 | 82.7
[28 empty] | 82.8 | 22960 | 82.8
[28 empty] | 82.9 | 23030 | 82.9
[28 empty] | 83 | 23100 | 83
[28 empty] | 83.1 | 23170 | 83.1
[28 empty] | 83.2 | 23240 | 83.2
[28 empty] | 83.3 | 23310 | 83.3
[28 empty] | 83.4 | 23380 | 83.4
[28 empty] | 83.5 | 23450 | 83.5
[28 empty] | 83.6 | 23520 | 83.6
[28 empty] | 83.7 | 23590 | 83.7
[28 empty] | 83.8 | 23660 | 83.8
[28 empty] | 83.9 | 23730 | 83.9
[28 empty] | 84 | 23800 | 84
[28 empty] | 84.1 | 23870 | 84.1
[28 empty] | 84.2 | 23940 | 84.2
[28 empty] | 84.3 | 24010 | 84.3
[28 empty] | 84.4 | 24080 | 84.4
[28 empty] | 84.5 | 24150 | 84.5
[28 empty] | 84.6 | 24220 | 84.6
[28 empty] | 84.7 | 24290 | 84.7
[28 empty] | 84.8 | 24360 | 84.8
[28 empty] | 84.9 | 24430 | 84.9
[28 empty] | 85 | 24500 | 85
[28 empty] | 85.1 | 24570 | 85.1
[28 empty] | 85.2 | 24640 | 85.2
[28 empty] | 85.3 | 24710 | 85.3
[28 empty] | 85.4 | 24780 | 85.4
[28 empty] | 85.5 | 24850 | 85.5
[28 empty] | 85.6 | 24920 | 85.6
[28 empty] | 85.7 | 24990 | 85.7
[28 empty] | 85.8 | 25060 | 85.8
[28 empty] | 85.9 | 25130 | 85.9
[28 empty] | 86 | 25200 | 86
[28 empty] | 86.1 | 25270 | 86.1
[28 empty] | 86.2 | 25340 | 86.2
[28 empty] | 86.3 | 25410 | 86.3
[28 empty] | 86.4 | 25480 | 86.4
[28 empty] | 86.5 | 25550 | 86.5
[28 empty] | 86.6 | 25620 | 86.6
[28 empty] | 86.7 | 25690 | 86.7
[28 empty] | 86.8 | 25760 | 86.8
[28 empty] | 86.9 | 25830 | 86.9
[28 empty] | 87 | 25900 | 87
[28 empty] | 87.1 | 25970 | 87.1
[28 empty] | 87.2 | 26040 | 87.2
[28 empty] | 87.3 | 26110 | 87.3
[28 empty] | 87.4 | 26180 | 87.4
[28 empty] | 87.5 | 26250 | 87.5
[28 empty] | 87.6 | 26320 | 87.6
[28 empty] | 87.7 | 26390 | 87.7
[28 empty] | 87.8 | 26460 | 87.8
[28 empty] | 87.9 | 26530 | 87.9
[28 empty] | 88 | 26600 | 88
[28 empty] | 88.1 | 26670 | 88.1
[28 empty] | 88.2 | 26740 | 88.2
[28 empty] | 88.3 | 26810 | 88.3
[28 empty] | 88.4 | 26880 | 88.4
[28 empty] | 88.5 | 26950 | 88.5
[28 empty] | 88.6 | 27020 | 88.6
[28 empty] | 88.7 | 27090 | 88.7
[28 empty] | 88.8 | 27160 | 88.8
[28 empty] | 88.9 | 27230 | 88.9
[28 empty] | 89 | 27300 | 89
[28 empty] | 89.1 | 27370 | 89.1
[28 empty] | 89.2 | 27440 | 89.2
[28 empty] | 89.3 | 27510 | 89.3
[28 empty] | 89.4 | 27580 | 89.4
[28 empty] | 89.5 | 27650 | 89.5
[28 empty] | 89.6 | 27720 | 89.6
[28 empty] | 89.7 | 27790 | 89.7
[28 empty] | 89.8 | 27860 | 89.8
[28 empty] | 89.9 | 27930 | 89.9
[28 empty] | 90 | 28000 | 90
[28 empty] | 90.1 | 28070 | 90.1
[28 empty] | 90.2 | 28140 | 90.2
[28 empty] | 90.3 | 28210 | 90.3
[28 empty] | 90.4 | 28280 | 90.4
[28 empty] | 90.5 | 28350 | 90.5
[28 empty] | 90.6 | 28420 | 90.6
[28 empty] | 90.7 | 28490 | 90.7
[28 empty] | 90.8 | 28560 | 90.8
[28 empty] | 90.9 | 28630 | 90.9
[28 empty] | 91 | 28700 | 91
[28 empty] | 91.1 | 28770 | 91.1
[28 empty] | 91.2 | 28840 | 91.2
[28 empty] | 91.3 | 28910 | 91.3
[28 empty] | 91.4 | 28980 | 91.4
[28 empty] | 91.5 | 29050 | 91.5
[28 empty] | 91.6 | 29120 | 91.6
[28 empty] | 91.7 | 29190 | 91.7
[28 empty] | 91.8 | 29260 | 91.8
[28 empty] | 91.9 | 29330 | 91.9
[28 empty] | 92 | 29400 | 92
[28 empty] | 92.1 | 29470 | 92.1
[28 empty] | 92.2 | 29540 | 92.2
[28 empty] | 92.3 | 29610 | 92.3
[28 empty] | 92.4 | 29680 | 92.4
[28 empty] | 92.5 | 29750 | 92.5
[28 empty] | 92.6 | 29820 | 92.6
[28 empty] | 92.7 | 29890 | 92.7
[28 empty] | 92.8 | 29960 | 92.8
[28 empty] | 92.9 | 30030 | 92.9
[28 empty] | 93 | 30100 | 93
[28 empty] | 93.1 | 30170 | 93.1
[28 empty] | 93.2 | 30240 | 93.2
[28 empty] | 93.3 | 30310 | 93.3
[28 empty] | 93.4 | 30380 | 93.4
[28 empty] | 93.5 | 30450 | 93.5
[28 empty] | 93.6 | 30520 | 93.6
[28 empty] | 93.7 | 30590 | 93.7
[28 empty] | 93.8 | 30660 | 93.8
[28 empty] | 93.9 | 30730 | 93.9
[28 empty] | 94 | 30800 | 94
[28 empty] | 94.1 | 30870 | 94.1
[28 empty] | 94.2 | 30940 | 94.2
[28 empty] | 94.3 | 31010 | 94.3
[28 empty] | 94.4 | 31080 | 94.4
[28 empty] | 94.5 | 31150 | 94.5
[28 empty] | 94.6 | 31220 | 94.6
[28 empty] | 94.7 | 31290 | 94.7
[28 empty] | 94.8 | 31360 | 94.8
[28 empty] | 94.9 | 31430 | 94.9
[28 empty] | 95 | 31500 | 95
[28 empty] | 95.1 | 31570 | 95.1
[28 empty] | 95.2 | 31640 | 95.2
[28 empty] | 95.3 | 31710 | 95.3
[28 empty] | 95.4 | 31780 | 95.4
[28 empty] | 95.5 | 31850 | 95.5
[28 empty] | 95.6 | 31920 | 95.6
[28 empty] | 95.7 | 31990 | 95.7
[28 empty] | 95.8 | 32060 | 95.8
[28 empty] | 95.9 | 32130 | 95.9
[28 empty] | 96 | 32200 | 96
[28 empty] | 96.1 | 32270 | 96.1
[28 empty] | 96.2 | 32340 | 96.2
[28 empty] | 96.3 | 32410 | 96.3
[28 empty] | 96.4 | 32480 | 96.4
[28 empty] | 96.5 | 32550 | 96.5
[28 empty] | 96.6 | 32620 | 96.6
[28 empty] | 96.7 | 32690 | 96.7
[28 empty] | 96.8 | 32760 | 96.8
[28 empty] | 96.9 | 32830 | 96.9
[28 empty] | 97 | 32900 | 97
[28 empty] | 97.1 | 32970 | 97.1
[28 empty] | 97.2 | 33040 | 97.2
[28 empty] | 97.3 | 33110 | 97.3
[28 empty] | 97.4 | 33180 | 97.4
[28 empty] | 97.5 | 33250 | 97.5
[28 empty] | 97.6 | 33320 | 97.6
[28 empty] | 97.7 | 33390 | 97.7
[28 empty] | 97.8 | 33460 | 97.8
[28 empty] | 97.9 | 33530 | 97.9
[28 empty] | 98 | 33600 | 98
[28 empty] | 98.1 | 33670 | 98.1
[28 empty] | 98.2 | 33740 | 98.2
[28 empty] | 98.3 | 33810 | 98.3
[28 empty] | 98.4 | 33880 | 98.4
[28 empty] | 98.5 | 33950 | 98.5
[28 empty] | 98.6 | 34020 | 98.6
[28 empty] | 98.7 | 34090 | 98.7
[28 empty] | 98.8 | 34160 | 98.8
[28 empty] | 98.9 | 34230 | 98.9
[28 empty] | 99 | 34300 | 99
[28 empty] | 99.1 | 34370 | 99.1
[28 empty] | 99.2 | 34440 | 99.2
[28 empty] | 99.3 | 34510 | 99.3
[28 empty] | 99.4 | 34580 | 99.4
[28 empty] | 99.5 | 34650 | 99.5
[28 empty] | 99.6 | 34720 | 99.6
[28 empty] | 99.7 | 34790 | 99.7
[28 empty] | 99.8 | 34860 | 99.8
[28 empty] | 99.9 | 34930 | 99.9
[28 empty] | 100 | 35000 | 100
[28 empty] | 100.1 | 35070 | 100.1
[28 empty] | 100.2 | 35140 | 100.2
[28 empty] | 100.3 | 35210 | 100.3
[28 empty] | 100.4 | 35280 | 100.4
[28 empty] | 100.5 | 35350 | 100.5
[28 empty] | 100.6 | 35420 | 100.6
[28 empty] | 100.7 | 35490 | 100.7
[28 empty] | 100.8 | 35560 | 100.8
[28 empty] | 100.9 | 35630 | 100.9
[28 empty] | 101 | 35700 | 101
[28 empty] | 101.1 | 35770 | 101.1
[28 empty] | 101.2 | 35840 | 101.2
[28 empty] | 101.3 | 35910 | 101.3
[28 empty] | 101.4 | 35980 | 101.4
[28 empty] | 101.5 | 36050 | 101.5
[28 empty] | 101.6 | 36120 | 101.6
[28 empty] | 101.7 | 36190 | 101.7
[28 empty] | 101.8 | 36260 | 101.8
[28 empty] | 101.9 | 36330 | 101.9
[28 empty] | 102 | 36400 | 102
[28 empty] | 102.1 | 36470 | 102.1
[28 empty] | 102.2 | 36540 | 102.2
[28 empty] | 102.3 | 36610 | 102.3
[28 empty] | 102.4 | 36680 | 102.4
[28 empty] | 102.5 | 36750 | 102.5
[28 empty] | 102.6 | 36820 | 102.6
[28 empty] | 102.7 | 36890 | 102.7
[28 empty] | 102.8 | 36960 | 102.8
[28 empty] | 102.9 | 37030 | 102.9
[28 empty] | 103 | 37100 | 103
[28 empty] | 103.1 | 37170 | 103.1
[28 empty] | 103.2 | 37240 | 103.2
[28 empty] | 103.3 | 37310 | 103.3
[28 empty] | 103.4 | 37380 | 103.4
[28 empty] | 103.5 | 37450 | 103.5
[28 empty] | 103.6 | 37520 | 103.6
[28 empty] | 103.7 | 37590 | 103.7
[28 empty] | 103.8 | 37660 | 103.8
[28 empty] | 103.9 | 37730 | 103.9
[28 empty] | 104 | 37800 | 104
[28 empty] | 104.1 | 37870 | 104.1
[28 empty] | 104.2 | 37940 | 104.2
[28 empty] | 104.3 | 38010 | 104.3
[28 empty] | 104.4 | 38080 | 104.4
[28 empty] | 104.5 | 38150 | 104.5
[28 empty] | 104.6 | 38220 | 104.6
[28 empty] | 104.7 | 38290 | 104.7
[28 empty] | 104.8 | 38360 | 104.8
[28 empty] | 104.9 | 38430 | 104.9
[28 empty] | 105 | 38500 | 105
[28 empty] | 105.1 | 38570 | 105.1
[28 empty] | 105.2 | 38640 | 105.2
[28 empty] | 105.3 | 38710 | 105.3
[28 empty] | 105.4 | 38780 | 105.4
[28 empty] | 105.5 | 38850 | 105.5
[28 empty] | 105.6 | 38920 | 105.6
[28 empty] | 105.7 | 38990 | 105.7
[28 empty] | 105.8 | 39060 | 105.8
[28 empty] | 105.9 | 39130 | 105.9
[28 empty] | 106 | 39200 | 106
[28 empty] | 106.1 | 39270 | 106.1
[28 empty] | 106.2 | 39340 | 106.2
[28 empty] | 106.3 | 39410 | 106.3
[28 empty] | 106.4 | 39480 | 106.4
[28 empty] | 106.5 | 39550 | 106.5
[28 empty] | 106.6 | 39620 | 106.6
[28 empty] | 106.7 | 39690 | 106.7
[28 empty] | 106.8 | 39760 | 106.8
[28 empty] | 106.9 | 39830 | 106.9
[28 empty] | 107 | 39900 | 107
[28 empty] | 107.1 | 39970 | 107.1
[28 empty] | 107.2 | 40040 | 107.2
[28 empty] | 107.3 | 40110 | 107.3
[28 empty] | 107.4 | 40180 | 107.4
[28 empty] | 107.5 | 40250 | 107.5
[28 empty] | 107.6 | 40320 | 107.6
[28 empty] | 107.7 | 40390 | 107.7
[28 empty] | 107.8 | 40460 | 107.8
[28 empty] | 107.9 | 40530 | 107.9
[28 empty] | 108 | 40600 | 108
[28 empty] | 108.1 | 40670 | 108.1
[28 empty] | 108.2 | 40740 | 108.2
[28 empty] | 108.3 | 40810 | 108.3
[28 empty] | 108.4 | 40880 | 108.4
[28 empty] | 108.5 | 40950 | 108.5
[28 empty] | 108.6 | 41020 | 108.6
[28 empty] | 108.7 | 41090 | 108.7
[28 empty] | 108.8 | 41160 | 108.8
[28 empty] | 108.9 | 41230 | 108.9
[28 empty] | 109 | 41300 | 109
[28 empty] | 109.1 | 41370 | 109.1
[28 empty] | 109.2 | 41440 | 109.2
[28 empty] | 109.3 | 41510 | 109.3
[28 empty] | 109.4 | 41580 | 109.4
[28 empty] | 109.5 | 41650 | 109.5
Formulas:
Estimated Storage = DATE(YEAR([Estimated Storage, row above]),MONTH([Estimated Storage, row above])+1,DAY([Estimated Storage, row above]))
Reservoir Storage Predictions = DATE(YEAR([Reservoir Storage Predictions, row below]),MONTH([Reservoir Storage Predictions, row below])-1,DAY([Reservoir Storage Predictions, row below]))
Reservoir Storage Predictions = DATE(YEAR([Reservoir Storage Predictions, row above]),MONTH([Reservoir Storage Predictions, row above])+1,DAY([Reservoir Storage Predictions, row above]))
Group Box 15
For off channel reservoirs. with (normally) constant levels, this table uses a pan evaporation and consumption (gals/MWh) to calculate the level and storage reductions
For sites with no level information use the conservation level and total depth to create a storage profile.
Select the evaporation location to use in calculations based on the geographic location of the reservoir in the state.
Consumption assumptions are based on information entered in the table in cells Q13:T17.
The monthly
change in storage after accounting for evaporation and consumption is used to forecast future storage in the reservoir.
This table predicts future storage based on the estimated storage in the table at left, and the profiles of montly changes estimated in the "Calculation of Drought Fit" table (columns AI to AR).
Because monitoring data is unavailable, the model assumes the reservoir is kept at constant levels.
This is the primary output of the prediction spreadsheet, indicating the number of months before the reservoir becomes at risk. The yellow dot indicates, should secondary water sources fail, the reservoir could become at risk within 12 months.
Note on BE3: Black & Veatch: Second Elevation column for calculations