## Slide 1: Planning Geomagnetic Disturbance Task Force (PGDTF) Update to the ROS
July 7, 2016
Michael Juricek
PGDTF Chairman
<number>
7/7/2016 ROS Meeting

## Slide 2: June 28, 2016 Meeting
Discussed PGRR046
Revised Draft of Procedure Manual
Discussed Next Activities
Mike Juricek – 7/7/2016 ROS Meeting
<number>

## Slide 3: TPL-007-1 Transmission System Planned Performance for Geomagnetic Disturbance Events
Applicability:
4.1. Functional Entities:
  4.1.1 Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2;
  4.1.2 Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2;
  4.1.3 Transmission Owner who owns a Facility or Facilities specified in 4.2;
  4.1.4 Generator Owner who owns a Facility or Facilities specified in 4.2.
  4.2. Facilities:
    4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV.
Mike Juricek – 7/7/2016 ROS Meeting
<number>

## Slide 4: Concerns Expressed by Some PGDTF Members
Rationale for a Geomagnetically Induced Current (GIC) System Model Below 200 kV.
Compliance Implications if GIC System Model Contains Facilities Below 200 kV.
Mike Juricek – 7/7/2016 ROS Meeting
<number>

## Slide 5: GIC System Model Below 200 kV
Reasons for Limiting GIC System Model to Above 200 kV
  Meets Requirements in Proposed Standard.
  Reduces Modeling Efforts of TSPs and GOs.
  Eliminates Modeling Requirement for TSPs and GOs with Facilities Below 200 kV.
Mike Juricek – 7/7/2016 ROS Meeting
<number>

## Slide 6: GIC System Model Below 200 kV
Rationale for Modeling All of the ERCOT Transmission System.
  The NERC Geomagnetic Disturbance Planning Guide States “In Some Systems it May Be Appropriate to Model the Network Below 200 kV.”
  Experienced GIC Modelers Support Complete System Model.
  70% of the 45,115 Miles of Transmission Lines in ERCOT Are Less Than 200 kV.
  The Number of High Side, Weye-Grounded ERCOT Transformers Is About Equal at 138 kV and 345 kV.
Mike Juricek – 7/7/2016 ROS Meeting
<number>

## Slide 7: GIC System Model Below 200 kV
  An Equivalent Model is Recommended for Excluded Transmission Systems.
  CenterPoint’s GIC Analysis Identified Two 138/69 kV Autotransformers and One 138-24 kV GSU in the List of the Top Ten Transformers with the Highest GICs.
  AEP’s GIC Analysis Showed About 60% of the Reactive Power Losses Occurred on Their 138 kV and 69 kV Systems.
  Most PGDTF Members Believe Modeling the Entire Transmission System is Technically Appropriate.
Mike Juricek – 7/7/2016 ROS Meeting
<number>

## Slide 8: GIC System Model Below 200 kV
  Most PGDTF Members Believe Modeling the Entire Transmission System is Needed to Accurately Determine the Impact of a Geomagnetic Disturbance (GMD) Event on the ERCOT System. Even if the GICs Are Not Large Enough to Cause Thermal Heating Issues for the Transformers, the Increased Reactive Power Losses Could Cause Unacceptable Loading on the Transformers and Unacceptable Voltage. The Voltage Analysis is Required by the Proposed Standard.
Mike Juricek – 7/7/2016 ROS Meeting
<number>

## Slide 9: Compliance Implications
  Some PGDTF Members Expressed Uncertainty Over Requiring More Modeling Than the Proposed Standard Requires.
  Some PGDTF Members Stated NERC Standards are Minimum Requirements.
  Some PGDTF Members Stated the ERCOT Transmission Planning Criteria and SSWG Base Cases Go Beyond the Requirements in TPL-001-4.
Mike Juricek – 7/7/2016 ROS Meeting
<number>

## Slide 10: Next Activities for PGDTF
Create GIC System Model for Geomagnetic Disturbance (GMD) Vulnerability Assessment (12/2016).
Proposed Standard Requires GIC System Model be Completed 18 Months After Approval of Standard.
Develop PGRR for Documenting GMD Planning Activities as Required by the Proposed Standard.
Mike Juricek – 7/7/2016 ROS Meeting
<number>

## Slide 11: Next Meeting
July ??, 2016 at Met Center
Continue Discussing Data Needed for the GIC System Model.
Develop Questions Regarding Use of the GIC Module.
Mike Juricek – 7/7/2016 ROS Meeting
<number>

## Slide 12: Questions and Answers
<number>
Mike Juricek – 7/7/2016 ROS Meeting