## Slide 1
ERCOT Independent Review of Riverton – Sand Lake 138kV Double Circuit Line
August 16, 2016

## Slide 2: Introduction
Load growth in the West Far West (WFW) study area has created the need for transmission improvements
The project establishes a new substation (Mentone SW) in a central load location of the Delaware Basin
  Low voltage issues in many buses on the Wink – Culberson – Yucca Drive Loop

## Slide 3: Transmission System Map of the Study Area

## Slide 4: Study Case
Base Case
  The 2018 and 2021 West Far West (WFW) summer peak cases from 2016 Regional Transmission Plan (RTP) were used to create base cases for this study
  IH-20 to Wickett upgrade left in the base case
    Undergoing RPG review
  Barrilla junction Project upgrade added to the base case
    Undergoing RPG review
  Oncor 2018 and 2021 load forecasts for the study area were used
  Castle Gap Solar Projects (16INR0065 and 16INR0065a) met Planning Guide 6.9 at the time of the study, therefore were added to the base case.
Criteria
  The reliability criteria used is consistent with the RTP study
  Single-Contingency (N-1) analysis was performed to study the conditions experienced in the Riverton-Sand Lake project report
    Inadequate system conditions resulting in voltage collapse

## Slide 5: Load Served in Wink – Culberson – Yucca Drive Loop
 | In 2018 16RTP | Oncor Load Forecast for 2018 | In 2021 16RTP | Oncor Load Forecast for 2021
Total (MVA): | 278.2 | 342.6 | 301.1 | 425.5

## Slide 6: Reliability Analysis of the Base Cases in the study Region
The project proposed addresses
the following Reliability issues:
  Low voltage issues in many
  buses on the
  Wink–Culberson–Yucca Drive Loop
  Connects a new load serving substation enabling service to current and future load
4 options considered
Bus | kV | Limit (p.u.) | N-1 | 
 |  |  | 2018 | 2021
MENTONE_SW_8 | 138 | 0.9 | - | 0.87
PYOTEWES_8 | 138 | 0.9 | - | 0.49
SALTCRKW_8 | 138 | 0.9 | - | 0.85
WHITOIL_8 | 138 | 0.9 | 0.58 | 0.45
ANADARKOT_8 | 138 | 0.9 | - | -
ANDRANCH_8 | 138 | 0.9 | - | 0.89
SANDBEND1_8 | 138 | 0.9 | 0.89 | 0.85
ORLA_SW1_8 | 138 | 0.9 | - | 0.86
RED_BLUFF1_8 | 138 | 0.9 | - | 0.86
BARSTOWNW_8 | 138 | 0.9 | - | -
SCRWBEAN_8 | 138 | 0.9 | - | 0.85
ELMAR_8 | 138 | 0.9 | - | 0.89
MASON_8 | 138 | 0.9 | - | 0.87
SCRWBEAN_T8 | 138 | 0.9 | - | 0.85
BLACKRVR_8 | 138 | 0.9 | 0.87 | 0.8
CULBERSON_8 | 138 | 0.9 | 0.86 | 0.8
SALTCREKSO_8 | 138 | 0.9 | 0.88 | 0.82
CULBER2119_8 | 138 | 0.9 | 0.88 | 0.83
L_CULBER8_1Y | 138 | 0.92 | 0.86 | 0.8

## Slide 7: Project Option 1
Build 25 mile 345kV operating at 138kV double circuit line from new switching stations Riverton to Sand Lake (Riverton – Mentone SW - Sand Lake)
Establish the new Mentone SW substation
Add 55.2MVAR Capacitor Bank in Whitoil (#1080)
Estimated cost is $46.2 million

## Slide 8: Project Option 2
Build 25 mile 138kV double circuit line from new switching stations Riverton to Sand Lake (Riverton – Mentone SW - Sand Lake)
Establish the new Mentone SW substation
Add 55.2MVAR Capacitor Bank in Whitoil (#1080)
Estimated cost is $27.2 million

## Slide 9: Project Option 3
Build 25 mile, 345kV operating at 138kV single circuit line from new switching stations Riverton to Sand Lake (Riverton – Mentone SW - Sand Lake) on a 345kV double circuit capable structure
Establish the new Mentone SW substation
Add 55.2MVAR Capacitor Bank in Whitoil (#1080)
Estimated cost is $40.2 million
Note: Supports Far West Project, in RPG review now, by creating 345kV structure that can be used for it.

## Slide 10: Project Option 4
Build 10 mile, 345 kV operating at138kV single circuit line from new switching stations Sand Lake to Mentone SW on a 345kV double circuit capable structure
Establish the new Mentone SW substation
Add an 80MVAR SVC (Static VAR Compensator) on Whitoil (#1080)
Estimated cost is $55.6 million

## Slide 11: Project Options Evaluation
All options address the low voltage issues in the Wink – Culberson – Yucca Drive loop in the 2021 summer peak base case used
Bus | kV | Limit (p.u.) | N-1 |  |  |  | 
 |  |  | Base Case | Op 1 | Op 2 | Op 3 | Op 4
MENTONE_SW_8 | 138 | 0.9 | 0.87 | - | - | - | -
PYOTEWES_8 | 138 | 0.9 | 0.49 | - | - | - | -
SALTCRKW_8 | 138 | 0.9 | 0.85 | - | - | - | -
WHITOIL_8 | 138 | 0.9 | 0.45 | - | - | - | -
ANADARKOT_8 | 138 | 0.9 | 0.9 | - | - | - | -
ANDRANCH_8 | 138 | 0.9 | 0.89 | - | - | - | -
SANDBEND1_8 | 138 | 0.9 | 0.85 | - | - | - | -
ORLA_SW1_8 | 138 | 0.9 | 0.86 | - | - | - | -
RED_BLUFF1_8 | 138 | 0.9 | 0.86 | - | - | - | -
BARSTOWNW_8 | 138 | 0.9 | 0.9 | - | - | - | -
SCRWBEAN_8 | 138 | 0.9 | 0.85 | - | - | - | -
ELMAR_8 | 138 | 0.9 | 0.89 | - | - | - | -
MASON_8 | 138 | 0.9 | 0.87 | - | - | - | -
SCRWBEAN_T8 | 138 | 0.9 | 0.85 | - | - | - | -
BLACKRVR_8 | 138 | 0.9 | 0.8 | - | - | - | -
CULBERSON_8 | 138 | 0.9 | 0.8 | - | - | - | -
SALTCREKSO_8 | 138 | 0.9 | 0.82 | - | - | - | -
CULBER2119_8 | 138 | 0.9 | 0.83 | - | - | - | -
L_CULBER8_1Y | 138 | 0.92 | 0.8 | - | - | - | -

## Slide 12: ERCOT Recommendation
ERCOT Recommends Option 3 as the preferred option to meet the reliability need in the area.
  Build 25 mile, 345kV operating at 138kV single circuit line from new switching stations Riverton to Sand Lake (Riverton – Mentone SW - Sand Lake) on a 345kV double circuit capable structure
  Establish the new Mentone SW substation
  Add 55.2MVAR Capacitor Bank in Whitoil (#1080)
Estimated cost is $40.2 million

## Slide 13: ERCOT Recommendation
ERCOT performed a sensitivity study where a case was simulated with load projections above the Oncor forecasted load for 2021:
The sensitivity study concluded that the addition of the potential load would require new 345 kV source in the area in addition to Option 3
Option 3 could be expanded to accommodate future 345 kV expansion of the area
 | Oncor Load Forecast for 2021 | Oncor Potential Load for 2021
Total (MVA): | 425.5 | 647

## Slide 14
?