## Slide 1
Discussion on Recent Reliability Unit Commitment Instructions
David Maggio and Chad Thompson
August 30th, 2016

## Slide 2: Introduction and Agenda
ERCOT staff received questions regarding recent Reliability Unit Commitment (RUC) instructions and was asked to discuss those instructions and our general process for committing Resources using the RUC application and process
RUC instructions from the following days will be discussed:
  August 6th, 2016
  August 7th, 2016
  August 10th, 2016
  May 30th, 2015
This will be followed by questions and additional group discussion

## Slide 3: August 6th, 2016 – Projected Congestion
August 6th was a high load day, particularly for a weekend day, and there were a number of congestion concerns
This congestion included the following transmission equipment:
  345 kV transmission line between the Singleton and Zenith substations
  138 kV transmission line between the Betka and Hockley substations
    This constraint was particularly difficult for RUC to resolve
  345 kV transmission line between the Twin Oak Switch and BTU Jack Creek substations
As a result of the projected congestion and Resource information in the Current Operating Plans (COPs), a number of commitments were recommended by RUC

## Slide 4: August 6th, 2016 – RUC Recommendations
Leading into the early morning hours of August 6th, RUC was recommending several Resources for commitment
  This included the current RMR Resource, some Combined Cycle Resources, and a number of shorter lead time Resources
2 of the 20 Resources recommended by RUC were selected by ERCOT (1 during midnight RUC execution and 1 during the 3 AM RUC execution)
  The shift factors for these Resources on the aforementioned constraints varied between -0.1% and -3.7% (SCED shift factors)
For the recommendations not selected, the decisions were largely based on using the RMR Resource as a last resort and on deferring the decision for shorter lead time Resources to allow the market to respond

## Slide 5: August 6th, 2016 – Real-Time Conditions
During the Operating Day, much of the projected congestion did materialize but was not generally at the shadow price caps
Differences in congestion largely due to Resource capacity increases that occurred between the RUC executions and real-time
  More than 400 MW of additional capacity from Resources with significant shift factors on congestion in the Houston area
Contingency | Constrained Element | Real-Time Market Congestion Rent ($)
DRNS_TB5 | SNGZEN99_A | 10,722,642.0
DSTEXP12 | BLESSI_LOLITA1_1 | 1,649,159.6
DJEWSNG5 | JK_TOKSW_1 | 1,293,141.1
DWH_STP5 | BONIVI_RINCON1_1 | 180,867.9
DKOCNUE8 | CHAMPL_WEIL_T1_1 | 113,382.5
SLAQLOB8 | BRUNI_69_1 | 50,261.7
BASE CASE | LISTON | 19,965.0
DFERPAL8 | 38T365_1 | 3,061.9
SLOCSPN9 | DENTON_AT1 | 1,283.0
DTRCELK5 | 1760__A | 0.0
DSNGZEN5 | BETHK_66_A | 0.0

## Slide 6: August 7th, 2016 – Projected Congestion
For August 7th, conditions were very similar to what was observed on the 6th
Many of the same constraints were being projected during the early morning to occur later that day, including the 3 mentioned for the 6th
Again, as a result of the projected congestion and Resource information in the COPs, a number of commitments were recommended by RUC

## Slide 7: August 7th, 2016 – RUC Recommendations
Leading into the early morning hours of August 7th, RUC was recommending several Resources for commitment
  This included Combined Cycle Resources and a number of shorter lead time Resources
1 of the 19 Resources recommended by RUC were selected by ERCOT (during 5 AM RUC execution)
  The shift factors for this Resource on the aforementioned constraints varied between -0.1% and -3.6% (SCED shift factors)
For the recommendations not selected, the decisions were largely based on deferring the decision for shorter lead time Resources to allow the market to respond

## Slide 8: August 7th, 2016 – Real-Time Conditions
During the Operating Day, much of the projected congestion did materialize but was not generally at the shadow price caps
Differences in congestion largely due to Resource capacity increases that occurred between the RUC executions and real-time
  More than 900 MW of additional capacity from Resources with significant shift factors on congestion in the Houston area
Contingency | Constrained Element | Real-Time Market Congestion Rent ($)
DRNS_TB5 | SNGZEN99_A | 4,523,204.2
DSTEXP12 | BLESSI_LOLITA1_1 | 1,184,354.9
DWH_STP5 | BONIVI_RINCON1_1 | 210,303.1
DJEWSNG5 | JK_TOKSW_1 | 171,695.0
SLAQLOB8 | BRUNI_69_1 | 70,323.9
DFL_MAR8 | BETHK_66_A | 55,246.6
BASE CASE | LISTON | 22,306.0
SE3S18 | PLESNTN_TORDLO_1 | 20,614.5
SBEVASH8 | BIG_COTU_1 | 6,744.8
DFERPAL8 | 38T365_1 | 3,396.1

## Slide 9: August 10th, 2016 – Projected Congestion
August 10th was one of the record setting high load days that was observed during that week
Congestion concerns for that day included the following pieces of transmission equipment:
  138 kV transmission line between the Ft. Worth and West Denton substations
  138/69 kV transformer at the Denton Steam substation
  138 kV transmission line between the West Denton and Jim Christal substations
Again, as a result of the projected congestion and Resource information in the COPs, a number of commitments were recommended by RUC

## Slide 10: August 10th, 2016 – RUC Recommendations
During the late morning and into the early afternoon, RUC was recommending several Resources for commitment
  This included Resources in the Ft. Worth/Denton area and the Houston area
Over the course of the day, 5 Resources were given RUC instructions by ERCOT based on some portion of the previously mentioned constraints (the first occurred at 9 AM and the final instruction was an extension on an earlier commitment and occurred at 7 PM)
  The shift factors for these Resources on the aforementioned constraints varied between -0.1% and -15.7% (SCED shift factors)
For the recommendations not selected, the decisions were largely based on deferring the decision for shorter lead time Resources to allow the market to respond

## Slide 11: August 10th, 2016 – Real-Time Conditions
Again, much of the projected congestion did materialize
  This specifically occurred for the Ft. Worth/Denton congestion and there was one constraint that had several consecutive intervals with a shadow price at the cap
Resource capacity increases between the RUC executions and real-time on the 10th were similar in size to what was observed on the 7th
Contingency | Constrained Element | Real-Time Market Congestion Rent ($)
SJMCW_D8 | FTW_W_DE_1 | 2,402,819.2
DCHBJOR5 | ATKRIN87_A | 140,222.0
DWH_STP5 | BONIVI_RINCON1_1 | 131,450.0
DFL_MAR8 | BETHK_66_A | 108,169.0
SLOCSPN9 | DENTON_AT1 | 89,650.2
SLAQLOB8 | BRUNI_69_1 | 81,925.9
BASE CASE | LISTON | 36,266.2
SFTWW_D8 | AIR_W_DE_1 | 30,629.1
DSTEXP12 | BLESSI_LOLITA1_1 | 30,213.2
DKOCNUE8 | CHAMPL_WEIL_T1_1 | 5,710.4
SSWDMGS8 | 6780__A | 2,177.7
DRNS_TB5 | SNGZEN99_A | 682.5
DFERPAL8 | 38T365_1 | 484.3

## Slide 12: May 30th, 2015 – RUC Instructions
For May 30th, 2015, the system conditions were somewhat different than what was observed in the August 2016 examples just discussed
  Although system load was much lower, there was significant congestion in the Houston area
11 Resources were given RUC instructions by ERCOT
  Significant real-time congestion was already being observed at the time of the instructions
  The instructions were all given during the 2 PM RUC execution for Resources that could start in the next hour or two
  The shift factors for these Resources on the relevant constraints were -14.1% or better (SCED shift factors)

## Slide 13: May 30th, 2015 – Real-Time Conditions
The real-time congestion was quite high for the Houston area
  The constraint for the 345 kV transmission line between the Singleton and Zenith substations had a significant number of intervals with the shadow price at the cap, particularly starting at 1:30 PM
Contingency | Constrained Element | Real-Time Market Congestion Rent ($)
DRNS_TB5 | SNGZEN99_A | 17,502,107.0
DJEWSNG5 | JK_TOKSW_1 | 4,316,458.5
BASE CASE | N_TO_H | 3,020,565.4
DGIBSNG5 | 260_A_1 | 809,032.8
DSTEXP12 | BLESSI_LOLITA1_1 | 305,789.0
DAUSSND5 | HWRDLN_1 | 16,271.6
BASE CASE | ZO_AJO | 3,069.5
SLAQLOB8 | BRUNI_69_1 | 2,277.4
SKEYWLV8 | 6610__D | 2,259.9
DMARZOR5 | 293T304_1 | 2,146.0
SSCUSUN8 | ROTN_WOLFGA1_1 | 775.3
SMARZOR5 | 419T419_1 | 683.4

## Slide 14: General RUC Process Comments
In cases in which a Resource under an RMR contract is recommended by RUC, ERCOT attempts to find alternative solutions using other available Resources
For RUC recommendations in which the lead time of the Resource(s) allows ERCOT to defer the commitment, ERCOT attempts to defer the decision to commit the Resource(s) based on the latest COP data
When real-time dispatch of online Resources is unable to resolve current congestion on the system, ERCOT will use the RUC process to commit offline and available Resources that can relieve the congestion

## Slide 15: Questions and Group Discussion