## Slide 1
UFR Deployments and the Reliability Adder
QMWG – August 30, 2016
ERCOT Staff

## Slide 2: Adding LR UFR Deployments to the Reliability Adder
Telemetry is available for all LRs providing RRS
  Resource Status – ONRL
  RRS Responsibility and RRS Schedule
  Net Power Consumption
  Low Power Consumption
  UFR Status – Armed or Online when active
  Circuit Breaker Status – Closed when active
RRS Schedules do not change during a UFR type deployment
No electronic instruction for dispatch or recall for UFR deployments – currently only have a verbal instruction for the recall
Ancillary Service Monitor relies on difference between RRS Responsibility and RRS Schedule to show quantity that has been deployed and as a result it does not show the amount deployed for UFR deployments
To add this capacity to the Reliability Adder, we need to identify a deployment trigger, a recall trigger and a way to measure the amount of capacity that tripped on under-frequency and its recovery following the recall. None of these items are currently in our systems today.

## Slide 3: Possible Approach to include UFR Load Deployments in the Reliability Price Adder
The following would only apply to LRs with ONRL COP status
Deployment Trigger
  New resource specific telemetry requirement signaling relay trip
  Many UFRs already have this capability
  Cost to implement for the Providers may be significant if field visits and relay changes are required
Capacity (MW)
  ERCOT Calculated Value
  Net Power Consumption (T-1 minute) – Net Power Consumption (NPC)
Recall Trigger
  Modification to the ERCOT Deployment Manger
  Add XML signal from the ERCOT Operator
Recovery Period
  Back out capacity using NPC and RRS Responsibility
Note: Additional emphasis should be added to require QSE’s to reflect schedule changes with UFR deployments and recovery of load following recall.

## Slide 4: Load Resource RRS UFR Deployments