## Slide 1
ERCOT Update on UFLS Annual Survey with TSP/DSP
Gene Lowrie
Reliability & Compliance Eng Sr.
July 2016

## Slide 2: Background on UFLS Survey Requirement
ERCOT coordinated and conducted an annual survey on May 12, 2016 with the TSPs and DSPs to ensure that the required automatic under-frequency load shed circuits were configured to provide the appropriate load relief in an under-frequency event as required by table below from Operating Guides 2.6.1(1) Requirements for Under-Frequency Load Shedding:
Operating Guide 2.6.1 (2) ERCOT will prior to the peak each year, survey each Distribution Service Provider’s (DSP’s) compliance with the automatic Load shedding steps above, and report its findings to the Technical Advisory Committee (TAC).

## Slide 3: Results of UFLS Survey Requirement
Below is a list of dates and activities reflecting the timeline and coordination of this survey:
03/24/2016 - ERCOT announcement of survey timeline and effort to OWG
04/01/2016 - ERCOT email notification sent by Client Services to TSP/DSP Authorized Representatives
05/12/2016 @ 11:00 AM- Date and time of the Survey
06/12/2016 - Survey results due back to ERCOT
August/September - Results compiled and being reported to OWG/ROS/TAC
Notes: Weather 5/12/2015 at 11:00 was mild again this year.

## Slide 4: Execution of UFLS Survey Requirement
The results of the 2016 requirement were successful and are reflected below:
Frequency response block | Minimum Requirement | Survey measurement
Block 1 response at 59.3 | 5% | 7.2%
Block 2 response at 58.9 | 10% | 12.2%
Block 3 response at 58.5 | 10% | 12.6%
Total | 25% | 31.9%
Two participants that did not meet their 5%, 10%, 10% breakdown, one due to outage on the relay equipment, the other is in the process of revising its UFLS Program. All participants met the 25% total.
In reference last year’s(2015) 25% total was 31.23%