## Info
Header Information
TDSP | Operator of the Major Transmission Element.
Major Transmission Element (MTE) | Transmission Element which was, or scheduled to be, on outage and has been associated with high congestion.
Equip. Type | Equipment Type of the MTE.
kV | Voltage Level of the MTE.
Congestion Year | Year when the associated congestion occurred.
Congestion Month | Month when the associated congestion occurred.
Contingency | Contingency associated with the MTE.
Overload | Overload associated with the MTE.
Source | Source of the information: 1 = Based on historical Real-Time congestion, 2 = Based on Outage Coordination Studies.
Outage Type | Outage Type is categorized to be either Planned (PL) and Forced (FR, FE, UE, M1, M2, M3)
Removal Request | This column will be filled with a "Y" when stakeholder(s) request to remove the MTE from the list.
Requestor | Stakeholder who is requesting to add or remove the MTE from the list (Organization, Person)
Reason for Addition | Justification for adding the MTE from the list.
Reason for Removal | Justification for removing the MTE from the list.
Decision | Final Decision of the Removal Request.
OCITF Consensus | Consensus after OCITF meetings.
Discussion Items | Any other information that stakeholder(s) want to discuss during the OCITF meetings.

## MTE(2015)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year | Congestion Month | Contingency | Overload | Source | Outage Type | Cancelled | Removal Request | Requestor | Reason for Removal | Decision | OCITF Consensus | Discussion Items
AEN | Austrop - Daffin | LN | 138 | 2015 | 5 | Howard Lane Tap - Wells Branch 138 kV | McNeil - Howard Lane Tap 138 kV | 1 | Planned | N
AEN | Austrop - Dunlap | LN | 138 | 2015 | 2 | DCKT Garfield LCRA to Lytton Springs and Austrop to Zorn 345 kV | Garfield AEN GF_AT_1 345/138 kV | 2 | Planned | N
AEN | Decker - Dunlap | LN | 138 | 2015 | 4, 5 | DCKT Hutto - Round Rock & Gabriel 138 kV | Gilleland - McNeil LCRA 138kV | 1, 2 | Planned | N
AEN | Dunlap - Techridge | LN | 138 | 2015 | 4, 5 | DCKT Hutto - Round Rock & Gabriel 138 kV | Gilleland - McNeil LCRA 138kV | 1, 2 | Planned | N
AEN | Garfield AEN - … - Onion Creek | LN | 138 | 2015 | 4 | DCKT Garfield LCRA to Lytton Springs and Austrop to Zorn 345 kV | Decker - Dunlap | 2 | Planned | N
AEN | Garfield AEN - Hicross | LN | 138 | 2015 | 4 | DCKT Garfield LCRA to Lytton Springs and Austrop to Zorn 345 kV | Decker - Dunlap | 2 | Planned | N
AEN | Hamilton AEN | CB | 138 | 2015 | 4 | DCKT Burleson - Carson Creek and Pedernales - Advanced Micro Devices 138 kV | Magnesium Plant - Northland 138kV | 1 | Forced | N
AEN | Sprinkle - Daffin Gin | LN | 138 | 2015 | 6 | DCKT Round Rock to Hutto and Gabriel 138 kV | Gilleland - McNeil LCRA 138 kV | 2 | Planned | N
AEN/LCRA | McNeil AEN - McNeil LCRA | LN | 138 | 2015 | 5 | Howard Lane Tap - Wells Branch 138 kV | McNeil - Howard Lane Tap 138 kV | 1, 2 | Planned | Y
AEP | Airline - Cabaniss | LN | 138 | 2015 | 10 | Alazan to Barney Davis 138 kV | Barney Davis - Rodd Field 138 kV | 2 | Planned | N
AEP | Azteca - SE Edinburg | LN | 138 | 2015 | 1, 2 | Rio Hondo (2H) Axfmr 345/138 kV | Aderhold - Elsa 138 kV | 1, 2 | Planned | N | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | Bessel - Lon Hill | LN | 138 | 2015 | 9 | Lobo 2_345_138 345/138 kV | Alice - North Ella 69 kV | 2 | Planned | N
AEP | Bruni - Crestonio | LN | 138 | 2015 | 5, 6 | Laquinta to Lobo 138 kV | Bruni 138_69_1 138/69 kV | 2 | Planned | Y, N
AEP | Coleto - Lon Hill | LN | 345 | 2015 | 3 | Coleto Creek to Pawnee Sw 345 kV | Kenedy Sw - Coleto Creek 138 kV | 2 | Planned | N
AEP | Duke - Azteca | LN | 138 | 2015 | 9 | DCKT North Edinburg to Palmhurst and West Ednburg 138 kV | Aderhold - Duke 138 kV | 2 | Planned | Y | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | Dupont Sw Ingleside - ... - Portland | LN | 138 | 2015 | 1 | DCKT Dupont Sw Ingleside to Whitepoint and Hecker 138 kV | Rincon - Whitepoint 138 kV | 2 | Planned | N
AEP | East Rio Hondo - … - Central Ave | LN | 138 | 2015 | 9 | Los Fresnos - Loma Alta Substation 138 kV | La Palma - Villa Cavazos 138 kV | 1 | Planned | N | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | Encinal - … - North Laredo Sw | LN | 138 | 2015 | 9 | Lobo 2_345_138 345/138 kV | Freer - San Diego 69 kV | 2 | Planned | Y
AEP | Falcon Sw - Roma Sw | LN | 138 | 2015 | 5 | Lobo 2_345_138 345/138 kV | Asherton - Catarina 138 kV | 2 | Planned | N | Y | AEP | PST should control the flow on Asherton-Catarina -ERCOT Procedure should handle |  | Leave it on
AEP | Gila - Hiway 9 | LN | 138 | 2015 | 10 | Koch Up River to Gila 138 kV | Morris Street - Gila 138 kV | 2 | Planned | N | Y | AEP | New config in fall with cable replaced |  | Remove
AEP | Gila - Koch Up River | LN | 138 | 2015 | 3, 11, 12 | Gila to Hiway 9 138 kV | Morris Street - Gila 138 kV | 2 | Planned | N | Y | AEP | New config in fall with cable replaced |  | Remove
AEP | La Palma - Rio Hondo | LN | 345 | 2015 | 7, 12 | La Palma - Rio Hondo 138 kV | Rio Hondo - East Rio Hondo 138 kV | 1, 2 | Forced | N | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | La Palma Bus #2 | BUS | 138 | 2015 | 10 | Laureles to La Palma 138 kV | Los Fresnos - Loma Alta 138 kV | 2 | Planned | N | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | Laureles - Port Isabel | LN | 138 | 2015 | 2 | Los Fresnos - Loma Alta Substation 138 kV | La Palma - Villa Cavazos 138 kV | 1 | Forced | N | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | Lobo - Laquinta | LN | 138 | 2015 | 5 | Crestonio to Falfurrias 138 kV | Bruni 138_69_1 138/69 kV | 2 | Planned | Y
AEP | Lobo - Laredo Vft North | LN | 138 | 2015 | 4 | Laredo VFT North to Lobo 138 kV | Asherton - Catarina 138 kV | 2 | Planned | N | Y | AEP | PST should control the flow on Asherton-Catarina -ERCOT Procedure should handle |  | Leave it on
AEP | Lobo - San Miguel | LN | 345 | 2015 | 11 | Rio Bravo - Zapata 138 kV | Freer - San Diego 69 kV | 2 | Planned | N
AEP | Lon Hill - Nelson Sharpe | LN | 345 | 2015 | 2, 10 | Ajo to Rio Hondo 345 kV | Celanese Bishop - Kleberg 138 kV | 2 | Planned | N
AEP | Lon Hill - Nueces Bay | LN | 138 | 2015 | 11, 12 | Gila to Hiway 9 138 kV | Morris Street - Gila 138 kV | 2 | Planned | N | Y | AEP | New config in fall with cable replaced |  | Remove
AEP | Lon Hill - Smith | LN | 69 | 2015 | 7 | Skidmore - Chase Field 69 kV | Orange Grove 69 Sub - Casa Blanca 69 kV | 1 | Planned | N | Y | AEP | STEC is rebuilding circuit? |  | Remove
AEP | Lon Hill Bus #1 | BUS | 138 | 2015 | 5 | Lobo 2_345_138 345/138 kV | Asherton - Catarina 138 kV | 2 | Planned | N | Y | AEP | PST should control the flow on Asherton-Catarina -ERCOT Procedure should handle |  | Leave it on
AEP | North Edinburg - Lon Hill | LN | 345 | 2015 | 3 | Nelson Sharpe to Ajo 345 kV | Celanese Bishop - Nelson Sharpe 138 kV | 2 | Planned | N
AEP | North Edinburg Auto #1 | XF | 345 | 2015 | 2 | North Edinburg 345_1382 345/138 kV | Burns Sub - Rio Hondo 138 kV | 2 | Planned | N | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | North Edinburg Auto #2 | XF | 345 | 2015 | 4, 5 | North Edinburg 345_138 345/138 kV | Burns Sub - Rio Hondo 138 kV | 2 | Planned | Y, Y | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | North Edinburg Bus #2 | BUS | 138 | 2015 | 2, 3 | McColl Road to North McAllen 138 kV | North Edinburg - North McAllen 138 kV | 2 | Planned | N, Y | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | Polk Ave - North Pharr | LN | 138 | 2015 | 5 | South Mission -Frontera (2)138/138 kV | North McAllen to West McAllen 138 kV | 1 | Planned | N | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | Rio Bravo - … - Wormser Rd | LN | 138 | 2015 | 2 | Bates - Frontera 138 kV | Frontera - Goodwin 138 kV | 1 | Planned | N | Y | AEP | Wind Gen on line will reduce the likely hood of this one |  | Leave it on
AEP | Rio Hondo - La Palma | LN | 345 | 2015 | 12 | La Palma - Rio Hondo 138 kV | Paredes Switching Station - Central Avenue Sub 138kV | 1 | Planned/Forced | N | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | San Angelo Concho - Rusthill | LN | 138 | 2015 | 6 | San Angelo College Hills 138_69T1 138/69 kV | SA Power 69T1 138/69 kV | 1 | Forced | N
AEP | San Angelo Concho Auto | XF | 138 | 2015 | 2, 6, 7 | San Angelo North 138_69T1 138/69kV | San Angelo College Hills 138_69T1 138/69 kV | 1 | Planned/Forced | N
AEP | Sinton - Skidmore | LN | 69 | 2015 | 1, 2, 3 | Orange Grove Switching Station - Lon Hill 138 kV | Lon Hill - Smith 69 kV | 1 | Planned/Forced | N | Y | AEP | series reactor in service and should reduce flow |  | Remove
AEP | South McAllen - West McAllen | LN | 138 | 2015 | 10 | Polk Avenue to North Pharr 138 kV | Palmhurst Tap - Key Sw 138 kV | 2 | Planned | N | Y | AEP | With new 345kv xvalley this is not as likely to occur |  | Remove
AEP | Stratton - King Ranch Gas Plant | LN | 138 | 2015 | 9 | Lobo 2_345_138 345/138 kV | Dilley Sw - Jardin 138 kV | 2 | Planned | N
AEP | West Batesville Bus #1 | BUS | 138 | 2015 | 4 | Lobo to San Miguel 345 kV | Hamilton Road - Maverick 138 kV | 2 | Planned | N
BRAZOS | Navo - Krugerville | LN | 138 | 2015 | 10 | Jim Christal Sub to West Denton 138 kV | Pockrus Sub - Teasley Sub 138 kV | 2 | Planned | N
BRAZOS | San Miguel Auto A | XF | 345 | 2015 | 3 | DCKT Lon Hill to North Edinburg 345 kV and Orange Grove Sw 138 kV | Fannin Sub - Victoria 69 kV | 2 | Planned | N
BRAZOS | San Miguel Auto B | XF | 345 | 2015 | 10 | Lobo 2_345_138 345/138 kV | San Miguel AUTA 345/138 kV | 2 | Planned | N
BRAZOS | Stephenville 138/69 Auto #1 | XF | 138 | 2015 | 3 | Oran Sub to Mineral Wells and RW Miller 138 kV | Bunker - RW Miller 138 kV | 2 | Planned | N
CNP | Cedar Bayou Plant - Decker | LN | 138 | 2015 | 3 | DCKT Cedar Bayou Plant to Baytown and Strang 138 kV | South Channel - Shell 138 kV | 2 | Planned | N
CNP | East Bernard - Orchard | LN | 138 | 2015 | 10 | South Lane City to Dyann 138 kV | Peters - Sealy 138 kV | 2 | Planned | Y
CNP | Fort Bend - Reading | LN | 138 | 2015 | 2 | DCKT Flewellen - Obrien and Mason Road 138 kV | Tomball - Hockley 138 kV | 1 | Planned | N
CNP | Gibbons Creek - Singleton (SNGXGC99) | LN | 345 | 2015 | 12 | DCKT Jewett - Singleton 345 kV | Singleton - Gibbons Creek 345kV (SNGXGC75) | 1, 2 | Planned | N
CNP | Jewett - Singleton (260) | LN | 345 | 2015 | 10 | DCKT Gibbons Creek - Singleton 345 kV | Jewett - Singleton 345 kV | 2 | Planned | N
CNP | Jewett - Limestone (225) | LN | 345 | 2015 | 3 | DCKT Limestone to Twin Oak Sw 345 kV | Big Brown - Jewett (50) | 2 | Planned | N
CNP | Jewett - Limestone (226) | LN | 345 | 2015 | 3 | DCKT Limestone to Twin Oak Sw 345 kV | Big Brown - Jewett (50) | 2 | Planned | N
CNP | PH Robinson - Center | LN | 345 | 2015 | 3 | DCKT Chambers to King and Cedar Bayou to Jordan 345 kV | Brine - Langston 138 kV | 2 | Planned | N
CNP | Singleton - Zenith (98_A) | LN | 345 | 2015 | 12 | DKCT Roans Prairie to Rothwood & Singleton-Tomball 345 kV | Singleton - Zenith 345kV (99_A) | 1, 2 | Planned | N
CNP | Singleton - Zenith (99_A) | LN | 345 | 2015 | 12 | DKCT Roans Prairie to Rothwood & Singleton-Tomball 345 kV | Singleton - Zenith 345kV (98_A) | 1, 2 | Planned | N
CNP | South Lane City - New Lane | LN | 138 | 2015 | 12 | DCKT Wharton to East Bernard and Dyann 138 kV (UNSOLVED) | N/A | 2 | Planned | N
CNP | White Oak - Jeanetta | LN | 345 | 2015 | 9 | DCKT Bellaire to WA Parish and Smithers 345 kV | Bellaire - Sharpstown 138 kV | 2 | Planned | N
CPS | Ballpark - … - Olmos | LN | 138 | 2015 | 5 | Calaveras to Walzem & Skyline 138kV | Ball Park - Fern 138 kV | 1 | Planned | N
CPS | Cagnon Auto #3 | XF | 345 | 2015 | 6 | Cagnon AXFMR1 345/138 kV | Cagnon AXFMR4 345/138 kV | 2 | Planned | Y
CPS | Cibolocr - ... - Green_Mt | LN | 138 | 2015 | 2 | DCKT Hill Country - Marion and Elmcreek 345 kV | Marion - Skyline 345 kV | 1 | Planned | N
CPS | Elmcreek - Hill Country | LN | 345 | 2015 | 10 | DCKT Marion to Hill Country and Skyline 345 kV | EC Mornhinweg - Parkway LCRA 138 kV | 2 | Planned | N
CPS | Hill Country Bus #1 | BUS | 138 | 2015 | 6 | Cagnon AXFMR1 345/138 kV | Cagnon AXFMR4 345/138 kV | 2 | Planned | Y
CPS | Laredo 1 - Five Pts | LN | 138 | 2015 | 5 | Calaveras to Walzem & Skyline 138kV | Ball Park - Fern 138 kV | 1 | Planned | N
CPS | Weiderstein - Randolph | LN | 138 | 2015 | 9 | DCKT Skyline to Harmony and Nacdches 138 kV | Fratt - Parkway LCRA 138 kV | 2 | Planned | Y
DME | Cooper Creek Sub - Industrial Sub | LN | 138 | 2015 | 7 | Lewisville Sw AXFMR22 345/138 kV | Pockrus Sub - Teasley Sub 138 kV | 2 | Planned | N
DME | Teasley - Forth Worth | LN | 138 | 2015 | 10 | Denton Arco to North Denton Interchange 138 kV | Hickory - Locust 69 kV | 2 | Planned | N
DME/TMPA | Cooper Creek Sub - … - Denton Arco | LN | 138 | 2015 | 7 | Lewisville Sw AXFMR22 345/138 kV | Pockrus Sub - Teasley Sub 138 kV | 2 | Planned | N
GAR | Firewheel - Olinger | LN | 138 | 2015 | 9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | 2 | Planned | N
GAR | Olinger - … - Elmgrove | LN | 138 | 2015 | 9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | 2 | Planned | N
GEUS/TMPA | Diesel - Greenville Steam | LN | 69 | 2015 | 7 | Shelby SHLBT1 138/69 kV | Greenville Steam T1 138/69 kV | 2 | Planned | N
LCRA | Bevo Auto #1 | XF | 138 | 2015 | 6 | Bevo Substation - Asherton 138 kV | Hamilton Road - Maverick 138 kV | 1 | Planned | N
LCRA | Clear Springs - Gilleland | LN | 345 | 2015 | 3 | Lytton Springs LY_AT2 345/138 kV | Lytton Springs LY_AT_1 345/138 kV | 2 | Planned | N
LCRA | Fayette Plant 1 - Fayette Plant 2 | LN | 345 | 2015 | 3 | DCKT Lost Pines to Austrop and Dunlap 345 kV | Fayetteville 26AT2 345/138 kV | 2 | Planned | N
LCRA | Fayette Plant 1 - Fayetteville | LN | 345 | 2015 | 2, 3 | DCKT Lost Pines - Austrop & Dunlop 345 kV | Fayette Plant 1 - Fayette Plant 2 345 kV | 1 | Planned | N
LCRA | Ferguson - Gillespie | LN | 138 | 2015 | 4 | DCKT Ferguson to Granite Mountain and Wirtz to Paleface 138 kV | Flat Rock - Wirtz 138 kV | 2 | Planned | Y
LCRA | Gilleland - McNeil LCRA | LN | 138 | 2015 | 6, 10 | Hutto Switch Axfmr 1 345/138 kV, DCKT Dunlap to Austrop and Lost Pines 345 kV | Gilleland - Pflugerville 138 kV, Austrop AU_AT1 345/138 kV | 1, 2 | Planned | N
LCRA | Gilleland Auto #1 | XF | 345 | 2015 | 10 | DCKT Marble Falls to Lakeway and Paleface to Wirtz 138 kV | Flat Rock - Wirtz 138 kV | 2 | Planned | N
LCRA | York Creek - Seguin | LN | 138 | 2015 | 9 | DCKT Zorn to Marion and Clear Springs 345 kV | Comal - Henne 138 kV | 2 | Planned | N
LCRA | Zorn - Hays Energy | LN | 345 | 2015 | 11 | Cagnon - Kendall 345 kV & Cico - Menger Creek 138 kV | Medina Lake - Pipe Creek 138 kV | 1 | Forced | N
LCRA | Zorn - Hutto | LN | 345 | 2015 | 3 | Lytton Springs LY_AT2 345/138 kV | Lytton Springs LY_AT_1 345/138 kV | 2 | Planned | N
LCRA | Zorn - Lytton Spring | LN | 345 | 2015 | 2 | Lytton Springs LY_AT1 or LY_AT2 345/138 kV | Lytton Springs LY_AT2 or LY_AT1 345/138 kV | 2 | Planned | N
ONCOR | Anna Sw - Valley SES | LN | 345 | 2015 | 10 | DCKT Valley South to Paris Sw and Valley SES 345 kV | Payne Sw - Memc West Tap 138 kV | 2 | Planned | Y
ONCOR | Argyle Bus #1 | BUS | 138 | 2015 | 8 | Jim Christal Sub to West Denton 138 kV | Pockrus Sub - Teasley Sub 138 kV | 2 | Planned | Y
ONCOR | Calmont Sw - … - Eagle Mountain (6190) | LN | 138 | 2015 | 6, 7 | DCKT Eagle Mountain SES - Parker Switch and Hicks Switch 345kv | Calmont Switch - Western Hills 138 kV (6185) | 1 | Planned/Forced | N
ONCOR | Cedar Crest Switch East Bus | BUS | 138 | 2015 | 9 | DCKT Mountain Creek to Cedar Hill Sw and Westmoreland 138 kV | West Levee Sw - Dallas West 138 kV | 2 | Planned | N |  | ONCOR |  |  | Further discuss tracking specific conditions | Oncor believes this congestion occurs only when Normally Open West Levee CB 025 is closed. Cedar Crest East Bus is only a HITE if CB 025 is closed during the outage.
ONCOR | Cedar Hill Sw - Mountain Creek | LN | 138 | 2015 | 9 | Polk Street to Oak Cliff South (6) 138 KV | Cedar Crest Switch - Oak Cliff South 138kV | 1, 2 | Planned | N
ONCOR | Centerville Road Sw - Forney Sw | LN | 345 | 2015 | 1 | DCKT Royse Sw to Forney Sw 345 kV | Forney Sw AXFMR3 345/138kV | 2 | Planned | N
ONCOR | Centerville Road Sw - Garland Road (3240_A) | LN | 138 | 2015 | 9 | DCKT Greenville Ave Sw to Parkdale Sw 138 kV | Centerville Road Sw - Garland Road (3250_A) | 2 | Planned | N
ONCOR | Cockrell Hill - Mountain Creek | LN | 138 | 2015 | 5 | DCKT Norwood Sw to Liggett Sw and Cedar Hill Sw 345 kV | Trinity River Authority - Mountain Creek 138 kV | 2 | Planned | Y
ONCOR | Cosden - Morgan Creek | LN | 138 | 2015 | 2, 4 | Barber Lake Sw to Morgan Creek 138 kV (14030 or 14035) | Barber Lake Sw - Morgan Creek 138 kV (14035 or 14030) | 2 | Planned | Y, N | Y | ONCOR | Resolved by the completion of the Dermott - Ennis Creek 138 kV line upgrade completed in Spring '15. |  | Remove
ONCOR | East Levee Sw - West Network | LN | 138 | 2015 | 5, 6 | DCKT West Levee Switch - 800/900 Network 138 kV | East Levee Switch - Reagan Street 138 kV (3410_A) | 1 | Planned | N |  | ONCOR |  |  | Further discuss tracking specific conditions | Oncor believes this congestion occurs only when Normally Open Lomo Alto CB 015 is closed. East Levee - West Network is only a HITE if CB 015 is closed during the outage.
ONCOR | East Levee Sw Bus West | BUS | 138 | 2015 | 11 | Norwood Sw AXFMR1 345/138 kV | Amelia Street - UT SW Medical Center (3415) | 2 | Planned | N
ONCOR | Elkton - Forney Sw | LN | 345 | 2015 | 4 | Tyler Grande to Martin Lake 345 kV | Elkton ACFMR3 345/138 kV | 2 | Planned | Y
ONCOR | Exxon Means Tap - Andrew North | LN | 138 | 2015 | 6 | Key Sub - Willow Valley Switch 138 kV | Getty Vealmoor - Getty Vealmoor Tap 138 kV | 1 | Forced | N | Y | ONCOR | Resolved by the upgrade of the Lamesa - Buzzard Draw 138 kV line rebuild completed in Fall '15. |  | Remove
ONCOR | Gunsight Sw - Getty Vealmoor | LN | 138 | 2015 | 6 | Key Sub - Willow Valley Switch 138 kV | Big Spring Crmwd Tap - Big Spring Switch 69 kV | 1 | Planned | N | Y | ONCOR | Resolved by the upgrade of the Lamesa - Buzzard Draw 138 kV line rebuild completed in Fall '15. |  | Remove
ONCOR | Jewett - Singleton (240) | LN | 345 | 2015 | 10 | DCKT Gibbons Creek - Singleton 345 kV | Jewett - Singleton 345 kV | 2 | Planned | N
ONCOR | Lake Creek Bus #1 | BUS | 138 | 2015 | 9 | Waco Mm Mars 2 to Robinson (6) 138 KV | Elm Mott - Northcrest Tap 138kV | 1, 2 | Planned | N
ONCOR | Lake Hubbard Bus #1 | BUS | 138 | 2015 | 5 | DCKT Lake Hubbard to Centerville Road and Centerville Road Sw 138 kV | Lake Hubbard - Saint Augustine Tap 138 kV | 2 | Planned | N
ONCOR | Lufkin Sw - Stryker Creek | LN | 345 | 2015 | 9, 10 | Nacogdoches Se - Mt Enterprise 345 kV | Centerville I45 - Pleasant Springs (Hcec) 138kV | 1 | Planned/Forced | N
ONCOR | Lufkin Sw Auto #1 | XF | 345 | 2015 | 10 | Nacogdoches Se - Mt Enterprise 345 kV | Centerville I45 - Pleasant Springs (Hcec) 138kV | 1 | Forced | N
ONCOR | Martin Lake Bus #1 | BUS | 345 | 2015 | 4 | DCKT Mt Enterprise to Trinidad and Martin Lake to Stryker Creek | Stryker Creek - Gresham Road Sw 138 kV | 2 | Planned | N
ONCOR | Morgan Creek - Sun Sw | LN | 138 | 2015 | 5 | Dermott Switch Ax1hh (3)345/138 kV | China Grove Switch - Snyder 138 kV | 1 | Planned | N | Y | ONCOR | Resolved by the completion of the Dermott - Ennis Creek 138 kV line upgrade completed in Spring '15. Also believe this congestion was caused by temporary configurations during the construction of that project. |  | Remove
ONCOR | Morgan Creek Bus #1 | BUS | 138 | 2015 | 10 | Willow Valley Switch to Wett Faraday 345 kV | Barber Lake Sw - Morgan Creek 138 kV (14030) | 2 | Planned | N | Y | ONCOR | Resolved by the completion of the Dermott - Ennis Creek 138 kV line upgrade completed in Spring '15. Also believe this congestion was caused by temporary configurations during the construction of that project. |  | Remove
ONCOR | Mountain Creek East Bus | BUS | 138 | 2015 | 11, 12 | Cedar Crest Sw - Mountain Creek 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV (3160) | 2 | Planned | N
ONCOR | Mountain Creek West Bus | BUS | 138 | 2015 | 10 | Irving Norwood to Norwood Sw 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV (3150) | 2 | Planned | N
ONCOR | Norwood Sw Auto #1 | XF | 345 | 2015 | 2 | DCKT Norwood Sw to Mountain Creek and East Levee Sw | Reagan Street - Amelia Street 138 kV | 2 | Planned | N
ONCOR | Norwood Sw Bus #1 | BUS | 345 | 2015 | 12 | Watermill Sw to Sargent Road and West Levee Sw 345 kV | Norwood Sw AXFMR1 345/138 kV | 2 | Planned | Y
ONCOR | Permian Basin - Wink Sub | LN | 138 | 2015 | 6 | Chevron Has - Wickett Whiting Oil 138 kV | Northward - Wink Sub 69 kV | 1 | Planned | N
ONCOR | Royse Sw Auto #1 | XF | 345 | 2015 | 9 | Royse Switch Axfmr3 345/138 KV | Forney Switch - Forney West 138kV | 1 | Planned | N
ONCOR | Sherry Sw - ... - Poly America | LN | 138 | 2015 | 5 | Cedar Hill Sw AXFMR2 345/138 kV | Park Row - Sherry Sw (6325) | 2 | Planned | N | Y | ONCOR | Resolved by completion of the Sherry - Cedar Hill upgrade project completed in May 2015 |  | Remove
ONCOR | Snyder - Sacroc | LN | 138 | 2015 | 9 | Dermott Switch Ax1hh (3)345/138 KV | Morgan Creek Ses - Sun Switch 138 kV | 1 | Planned | N | Y | ONCOR | Resolved by the completion of the Dermott - Ennis Creek 138 kV line upgrade completed in Spring '15. Also believe this congestion was caused by temporary configurations during the construction of that project. |  | Remove
ONCOR | Temple Sw - Bell County East Sw | LN | 345 | 2015 | 3 | Navarro - Watermill Switch 345 kV | Big Brown - Richland Chambers 345 kV | 1 | Planned | N
ONCOR | Valley SES Bus #2 (West) | BUS | 138 | 2015 | 8 | Valley South to Anna Sw and Farmersville Sw 345 kV | Pink Hills Pod - Payne Sw 138 kV | 2 | Planned | Y
ONCOR | Venus Sw Bus #1 (North) | BUS | 345 | 2015 | 7 | Limits Generation |  | 2 | Planned | N
ONCOR | Watermill Sw - Sargent Road | LN | 345 | 2015 | 3 | Topeka Termination - West Levee Switch 345 kV | Cedar Hill Switch - Mountain Creek 138 kV | 1 | Planned | N | Y | ONCOR | Expected to be resolved by the completion of the Cedar Hill - Mountain Creek 138 kV line upgrade. Expected completion Fall '16. |  | Non-Consensus
ONCOR | Watermill Sw - West Levee Sw | LN | 345 | 2015 | 3 | Topeka Termination - West Levee Switch 345 kV | Cedar Hill Switch - Mountain Creek 138 kV | 1 | Planned | N | Y | ONCOR | Expected to be resolved by the completion of the Cedar Hill - Mountain Creek 138 kV line upgrade. Expected completion Fall '16. |  | Non-Consensus
SHARL | Grandview Wind Farm - Alibates | LN | 345 | 2015 | 5 | Isolates Generation |  | 2 | Planned | N
SHARL | Tule Canyon - White River | LN | 345 | 2015 | 11, 12 | Panhandle GTC | N/A | 1, 2 | Planned | Y, N
SHARL | Tule Canyon BUS #1 | BUS | 345 | 2015 | 6 | Panhandle GTC | N/A | 2 | Planned | N
SHARL | Tule Canyon BUS #2 | BUS | 345 | 2015 | 6 | Panhandle GTC | N/A | 2 | Planned | N
SHARL/WETT | White River - WETT Cottonwood | LN | 345 | 2015 | 11, 12 | Panhandle GTC | N/A | 1, 2 | Planned | N
STEC | East Rio Hondo - … - Central Ave | LN | 138 | 2015 | 5, 9 | Los Fresnos - Loma Alta Substation 138 kV | La Palma - Villa Cavazos 138 kV | 1, 2 | Planned | N
STEC | Sam Rayburn - Vanderbilt | LN | 138 | 2015 | 10 | Loop 463 to Sam Rayburn 138 kV | Rayburn 138_69_2 138/69 kV | 2 | Planned | N
TMPA | North Denton - Denton Arco | LN | 138 | 2015 | 7 | DCKT Lewisville Switch - Krum West Switch and Roanoke Switch 345 kV | Teasley Substaion - Pockrus Substation 138 k | 1 | Forced | N
TMPA | Olinger - … - Pruitt | LN | 138 | 2015 | 7 | Basecase | Low Voltage at Pruitt 138 kV | 2 | Planned | Y
TNMP | Dickinson - Freeway Park | LN | 138 | 2015 | 8 | North Alvin Tnp to Meadow 138 KV | PH Robinson to Southshore TNP 138 kV | 1 | Forced | N

## Request for Addition
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Requestor | Reason for Addition | Decision