## Summary
Release Date: September 1, 2016
PRELIMINARY
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Winter 2016/2017
SUMMARY
The ERCOT Region is expected to have sufficient installed generating capacity to serve the forecasted peak demand in the upcoming winter season (December 2016 through February 2017). The forecasted peak demand of 58,591 MW is based on expected winter peak weather conditions. ERCOT also expects that 1,189 MW of planned winter-rated capacity will be added by the start of the winter season.
Based on the scenarios evaluated, an extreme higher-than-normal number of forced generation outages occurring during a period of unusually high demand would be unlikely to result in insufficient resources being available to serve those demands. Even if those conditions coincide with extremely low temperatures and associated capacity reductions resulting from natural gas curtailments, current information indicates that there would be sufficient generation available on a systemwide basis.
This preliminary winter SARA report includes a unit outage forecast of 8,534 MW developed from historical winter season outage data gathered since the start of the Texas Nodal Market in December 2010. Extreme outage scenarios increase that total to more than 13,600 MW.
Although ERCOT has not been notified of changes to available generation capacity for the winter season associated with regulatory requirements, it continues to monitor and consult with generation resource owners regarding their regulatory compliance plans.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Winter 2016/2017 - Preliminary
Release Date: September 1, 2016
Forecasted Capacity and Demand
|  | Operational Resources (excluding wind), MW | 68706.94 | Based on current ratings reported through the unit registration process
|  | Switchable Capacity Total, MW | 3763 | Rated capacity of resources that can interconnect with other regions and are available to ERCOT
|  | less Switchable Capacity Unavailable to ERCOT, MW | -490 | Based on survey responses of Switchable Resource owners
|  | Mothball Resources, MW | 0 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
|  | Private Use Network Capacity Contribution, MW | 4436 | Average capability of the top 20 hours in the winter peak seasons for the past three years
|  | Non-Coastal Wind Resources Capacity Contribution, MW | 2923.58 | Based on 20% of rated capacity for non-coastal wind resources per Nodal Protocols Section 3.2.6.2.2
|  | Coastal Wind Resources Capacity Contribution, MW | 716.59 | Based on 35% of rated capacity for coastal wind resources per Nodal Protocols Section 3.2.6.2.2
|  | Solar Utility-Scale, Peak Average Capacity Contribution, MW | 14.385 | Based on 5% of rated capacity for solar resources per Nodal Protocols Section 3.2.6.2.2
|  | RMR Resources to be under Contract, MW | 0 | Gas-fired unit (371 MW) placed under RMR contract on June 2, 2016; not available during winter season
|  | Non-Synchronous Ties Capacity Contribution, MW | 246.4 | Average capability of the top 20 hours in the winter peak seasons for the past three years
|  | Planned Thermal Resources with Signed IA, Air Permits and Water Rights, MW | 615 | Based on projected dates provided by developers of generation resources
|  | Planned Non-Coastal Wind, MW | 536.06 | Based on projected dates and 20% of rated capacity for non-coastal wind resources
|  | Planned Coastal Wind, MW | 0 | Based on projected dates and 35% of rated capacity for coastal wind resources
|  | Planned Solar Utility-Scale with signed IA, MW | 37.72 | Based on 5% of rated capacity for solar resources per Nodal Protocols Section 3.2.6.2.2
| [a] Total Resources, MW |  | 81467.955
| [b] Peak Demand, MW |  | 58591 | Peak forecast is based on expected weather conditions for winter 2016/2017
| [c] Reserve Capacity [a - b], MW |  | 22876.955
Range of Potential Scenarios
|  |  | Forecasted Season Peak Load | Extreme Load / Typical Generation Outages | Extreme Load / Extreme Generation Outages
|  | Peak Load Adjustment | 0 | 7118 | 7118 | Winter Peak Load Extreme Forecast is 65,709 MW, and is based on 2011 winter weather conditions
|  | Typical Maintenance Outages | 4291 | 4291 | 4291 | Based on historical average of planned outages for December through February weekdays (starting in 2010)
|  | Typical Forced Outages (2) | 4243 | 5755 | 5755 | Based on historical average of forced outages for December through February weekdays (starting in 2010); both Extreme Load scenarios include typical outages/derates due to natural gas curtailments during extreme peak load hours
|  | Extreme Forced Outages (90th Percentile) | 0 | 0 | 3586 | Based on historical forced outages at the 90% confidence interval plus additional derates due to natural gas curtailments resulting from combined low ambient temperatures and extreme peak loads
| [d] Total Uses of Reserve Capacity |  | 8534 | 17164 | 20750
| [e] Capacity Available for Operating Reserves (c-d), MW |  | 14342.955 | 5712.955 | 2126.955
Less than 2,300 MW indicates risk of EEA1

## Winter_Capacities
Unit Capacities - Winter
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | START YEAR | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1235
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1225
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1350
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1354
8 | BIG BROWN U1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 606
9 | BIG BROWN U2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 602
10 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 660
11 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 603
12 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 605
13 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 449
14 | GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470
15 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
16 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775
17 | J T DEELY U1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 420
18 | J T DEELY U2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420
19 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831
20 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858
21 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815
22 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
23 | MONTICELLO U1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 580
24 | MONTICELLO U2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 580
25 | MONTICELLO U3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795
26 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840
27 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825
28 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
29 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
30 | SANDOW U5 |  | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 600
31 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970
32 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 158
33 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 158
34 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 659
35 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 658
36 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577
37 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610
38 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 149
39 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 149
40 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 160
41 | BARNEY M DAVIS REPOWER CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 165
42 | BARNEY M DAVIS REPOWER CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 165
43 | BARNEY M DAVIS REPOWER STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 325
44 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 167
45 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 167
46 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 234
47 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 170.9
48 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 85.2
49 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 170.9
50 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 168.5
51 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 226.7
52 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 168
53 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 168
54 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270
55 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 77.5
56 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 77.5
57 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 74
58 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 173
59 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 173
60 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 186
61 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 79
62 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 72
63 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 102
64 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 77
65 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 73
66 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 108
67 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 191
68 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 189
69 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 189
70 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 146
71 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 203
72 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 215
73 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 203
74 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 215
75 | DEER PARK ENERGY CENTER STG |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290
76 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 190
77 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 231
78 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 127
79 | FERGUSON REPLACEMENT CTG1 |  | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 186.1
80 | FERGUSON REPLACEMENT CTG2 |  | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 186.1
81 | FERGUSON REPLACEMENT STG |  | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 194.9
82 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 192
83 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 184
84 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 184
85 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 192
86 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 184
87 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 184
88 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 420
89 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 420
90 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 160.7
91 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 160.7
92 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 179.8
93 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 161.1
94 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 161.1
95 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 179.7
96 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 167
97 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 167
98 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 167
99 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 167
100 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 203
101 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 203
102 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 237
103 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 237
104 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 247
105 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 247
106 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 150
107 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 150
108 | HIDALGO ENERGY CENTER STG |  | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 176
109 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 165
110 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 165
111 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 310
112 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 165
113 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 165
114 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 310
115 | JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 177
116 | JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
117 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 186
118 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 176
119 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 176
120 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 186
121 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
122 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
123 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 183
124 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 183
125 | LOST PINES POWER STG |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 192
126 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 218.6
127 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 218.6
128 | MAGIC VALLEY STATION STG |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 257.9
129 | MIDLOTHIAN ENERGY FACILITY CS 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 240
130 | MIDLOTHIAN ENERGY FACILITY CS 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 240
131 | MIDLOTHIAN ENERGY FACILITY CS 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 240
132 | MIDLOTHIAN ENERGY FACILITY CS 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 240
133 | MIDLOTHIAN ENERGY FACILITY CS 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 257
134 | MIDLOTHIAN ENERGY FACILITY CS 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 257
135 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 165
136 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 165
137 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 325
138 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 157.9
139 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 151.5
140 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 154
141 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 152.3
142 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 212
143 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 212
144 | PANDA SHERMAN POWER CTG1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 218.5
145 | PANDA SHERMAN POWER CTG2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 218.5
146 | PANDA SHERMAN POWER STG |  | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 333.6
147 | PANDA TEMPLE I POWER CTG1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 218.5
148 | PANDA TEMPLE I POWER CTG2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 218.5
149 | PANDA TEMPLE I POWER STG |  | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 333.6
150 | PANDA TEMPLE II POWER CTG1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 218.5
151 | PANDA TEMPLE II POWER CTG2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 218.5
152 | PANDA TEMPLE II POWER STG |  | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 333.6
153 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 87
154 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 87
155 | PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 89
156 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 176
157 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 176
158 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 169
159 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 84
160 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 86
161 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
162 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 81
163 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 81
164 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
165 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 175
166 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 175
167 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 175
168 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323
169 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
170 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 51
171 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
172 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
173 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 170
174 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 160
175 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 21
176 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 49
177 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57
178 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57
179 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57
180 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57
181 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104
182 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57
183 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57
184 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57
185 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57
186 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104
187 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 102.4
188 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 102.4
189 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 102.4
190 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.5
191 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 171
192 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 132
193 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20
194 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20
195 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20
196 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 16
197 | WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 275
198 | WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 275
199 | WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 290
200 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 249
201 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 249
202 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 293
203 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 20
204 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 48
205 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 50
206 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 54
207 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 54
208 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 54
209 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 54
210 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 80
211 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 79
212 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 78
213 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 77
214 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 170.4
215 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 170.4
216 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 45
217 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 45
218 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 45
219 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 45
220 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 54
221 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 54
222 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 54
223 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 58
224 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 64
225 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 54
226 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.4
227 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.4
228 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.4
229 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 97.4
230 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 94.4
231 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 45
232 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46
233 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 44
234 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46
235 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 81
236 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 81
237 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 81
238 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 81
239 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 81
240 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 81
241 | PEARSALL IC ENGINE PLANT A |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
242 | PEARSALL IC ENGINE PLANT B |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
243 | PEARSALL IC ENGINE PLANT C |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
244 | PEARSALL IC ENGINE PLANT D |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
245 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 71
246 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 71
247 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 74
248 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 75
249 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 75
250 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 1994 | 115
251 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 1994 | 115
252 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 84
253 | SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 13.5
254 | SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 13.5
255 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81
256 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81
257 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 48
258 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 48
259 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 48
260 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 48
261 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 48
262 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 48
263 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46
264 | SKY GLOBAL POWER ONE A |  | SKY1_SKY1A | COLORADO | GAS | SOUTH | 2016 | 26.7
265 | SKY GLOBAL POWER ONE B |  | SKY1_SKY1B | COLORADO | GAS | SOUTH | 2016 | 26.7
266 | T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57
267 | T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57
268 | T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57
269 | T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57
270 | T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57
271 | T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57
272 | T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
273 | TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 89
274 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
275 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
276 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
277 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47
278 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13
279 | W A PARISH - PETRA NOVA CTG |  | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 88
280 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 46
281 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 46
282 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 46
283 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 46
284 | B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 330
285 | CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
286 | CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
287 | DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 110
288 | DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 320
289 | DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 428
290 | GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234
291 | GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
292 | HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
293 | HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
294 | HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
295 | LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
296 | LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523
297 | MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122
298 | MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118
299 | MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568
300 | O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
301 | O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410
302 | PEARSALL STG U1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 20
303 | PEARSALL STG U2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 24
304 | PEARSALL STG U3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 22
305 | POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 20
306 | POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 26
307 | POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41
308 | R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 1968 | 75
309 | R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 1972 | 120
310 | R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 1975 | 208
311 | RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
312 | RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
313 | RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
314 | SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
315 | SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135
316 | SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 340
317 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 61
318 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
319 | STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
320 | STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
321 | TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235
322 | V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220
323 | V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
324 | V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
325 | W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169
326 | W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169
327 | W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 258
328 | W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 552
329 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
330 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
331 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
332 | FORT WORTH METHANE LFG |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6
333 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
334 | MCKINNEY LFG |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2
335 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.24
336 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
337 | TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2
338 | VIRIDIS ENERGY-ALVIN LFG |  | DG_AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7
339 | VIRIDIS ENERGY-HUMBLE LFG |  | DG_HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10
340 | VIRIDIS ENERGY-LIBERTY LFG |  | DG_LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9
341 | VIRIDIS ENERGY-TRINITY BAY LFG |  | DG_TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9
342 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
343 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
344 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
345 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
346 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
347 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2012 | 0
348 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 68439.84
349
350 | Operational Resources (Hydro)
351 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
352 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
353 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
354 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
355 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
356 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
357 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
358 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
359 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
360 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
361 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
362 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
363 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
364 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
365 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
366 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
367 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
368 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
369 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
370 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29
371 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 24
372 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 24
373 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.35
374 | EAGLE PASS HYDRO |  | DG_EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
375 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | DG_CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
376 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
377 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
378 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
379 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
380 | Operational Capacity Total (Hydro) | [6 empty] | 555.05
381 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 442.1
382
383 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | -175
384 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 68706.94
385
386 | Operational Resources (Switchable)
387 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 178
388 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 180
389 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 307
390 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 178
391 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 180
392 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 307
393 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 180
394 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 180
395 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 180
396 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400
397 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 162
398 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 179
399 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 178
400 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 389
401 | FRONTERA GENERATION CTG 1 |  | FRONTERA_FRONTEG1 | HIDALGO | GAS | SOUTH | 1999 | 0
402 | FRONTERA GENERATION CTG 2 |  | FRONTERA_FRONTEG2 | HIDALGO | GAS | SOUTH | 1999 | 0
403 | FRONTERA GENERATION STG |  | FRONTERA_FRONTEG3 | HIDALGO | GAS | SOUTH | 2000 | 0
404 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS | WEST | 2016 | 195
405 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 195
406 | ELK STATION CTG 3 |  | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 195
407 | Switchable Capacity Total | [6 empty] | 3763
408
409 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  | GAS |  |  | -490
410
411 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | COAL |  |  | 0
412
413 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 4428
414 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | 8
415
416 | Operational Resources (Wind)
417 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8
418 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND | NORTH | 2007 | 120
419 | BLUE SUMMIT WIND 5 |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9
420 | BLUE SUMMIT WIND 6 |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4
421 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND | WEST | 2012 | 150
422 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND | PANHANDLE | 2015 | 149.8
423 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6
424 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5
425 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117
426 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2
427 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88
428 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90
429 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114
430 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5
431 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120
432 | CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5
433 | CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186
434 | CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5
435 | CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | COKE | WIND | WEST | 2008 | 112.5
436 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75
437 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75
438 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND | WEST | 2008 | 126.5
439 | DESERT SKY WIND 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84
440 | DESERT SKY WIND 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5
441 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND | PANHANDLE | 2016 | 100.2
442 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND | PANHANDLE | 2016 | 100.2
443 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7
444 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2
445 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80
446 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6
447 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6
448 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 107.4
449 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND | PANHANDLE | 2014 | 103.8
450 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND | WEST | 2003 | 99
451 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND | WEST | 2003 | 61
452 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND | WEST | 2015 | 150
453 | GREEN PASTURES WIND 2 |  | GPASTURE_WIND_II | BAYLOR | WIND | WEST | 2015 | 150
454 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5
455 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND | PANHANDLE | 2015 | 99.9
456 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND | PANHANDLE | 2015 | 100
457 | HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6
458 | HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 158
459 | HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5
460 | HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115
461 | INADALE WIND |  | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6
462 | INDIAN MESA WIND |  | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5
463 | JAVELINA WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND | SOUTH | 2015 | 19.7
464 | JAVELINA WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND | SOUTH | 2015 | 230
465 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND | PANHANDLE | 2015 | 146.2
466 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND | PANHANDLE | 2015 | 153.6
467 | KEECHI WIND 138 KV JOPLIN |  | KEECHI_U1 | JACK | WIND | NORTH | 2015 | 110
468 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3
469 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3
470 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3
471 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3
472 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155
473 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND | NORTH | 2015 | 103.8
474 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND | NORTH | 2015 | 106.3
475 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200
476 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100
477 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100
478 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND | PANHANDLE | 2015 | 100
479 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND | PANHANDLE | 2015 | 100
480 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5
481 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51
482 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5
483 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24
484 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND | SOUTH | 2015 | 200
485 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND | WEST | 2015 | 105.6
486 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND | WEST | 2015 | 105.6
487 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND | PANHANDLE | 2014 | 144.3
488 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND | PANHANDLE | 2014 | 144.3
489 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND | PANHANDLE | 2008 | 150
490 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND | WEST | 2009 | 92.6
491 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND | WEST | 2009 | 60
492 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8
493 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2
494 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2
495 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 94.2
496 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 96.6
497 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5
498 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5
499 | PANTHER CREEK WIND 3 |  | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5
500 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5
501 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2
502 | PYRON WIND |  | PYR_PYRON1 | SCURRY | WIND | WEST | 2008 | 249
503 | RATTLESNAKE DEN WIND PHASE 1 G1 |  | RSNAKE_G1 | GLASSCOCK | WIND | WEST | 2015 | 104.3
504 | RATTLESNAKE DEN WIND PHASE 1 G2 |  | RSNAKE_G2 | GLASSCOCK | WIND | WEST | 2015 | 103
505 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84
506 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209
507 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND | PANHANDLE | 2015 | 150
508 | SAND BLUFF WIND |  | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90
509 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND | SOUTH | 2015 | 76
510 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND | NORTH | 2012 | 150
511 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND | WEST | 2015 | 204.1
512 | SHERBINO 1 WIND |  | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150
513 | SHERBINO 2 WIND |  | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 147.5
514 | SILVER STAR WIND |  | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60
515 | SNYDER WIND |  | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63
516 | SOUTH PLAINS WIND I |  | SPLAIN1_WIND1 | FLOYD | WIND | PANHANDLE | 2015 | 102
517 | SOUTH PLAINS WIND 2 |  | SPLAIN1_WIND2 | FLOYD | WIND | PANHANDLE | 2015 | 98
518 | SOUTH PLAINS WIND II A |  | SPLAIN2_WIND21 | FLOYD | WIND | PANHANDLE | 2016 | 148.5
519 | SOUTH PLAINS WIND II B |  | SPLAIN2_WIND22 | FLOYD | WIND | PANHANDLE | 2016 | 151.8
520 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND | WEST | 2008 | 98.2
521 | SPINNING SPUR WIND TWO |  | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161
522 | SPINNING SPUR 3 [WIND 1] |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND | PANHANDLE | 2015 | 96
523 | SPINNING SPUR 3 [WIND 2] |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND | PANHANDLE | 2015 | 98
524 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120
525 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND | WEST | 2014 | 211.2
526 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND | WEST | 2015 | 164.7
527 | SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.6
528 | SWEETWATER WIND 2A |  | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 18.1
529 | SWEETWATER WIND 2B |  | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 105
530 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5
531 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5
532 | SWEETWATER WIND 4-5 |  | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.2
533 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.7
534 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8
535 | TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7
536 | TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6
537 | TRENT WIND |  | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150
538 | TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | YOUNG | WIND | WEST | 2012 | 117.5
539 | TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | YOUNG | WIND | WEST | 2012 | 107.5
540 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5
541 | WEST TEXAS WIND |  | SW_MESA_SW_MESA | UPTON | WIND | WEST | 1999 | 80.3
542 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND | PANHANDLE | 2007 | 57
543 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND | SOUTH | 2012 | 91
544 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND | WEST | 2014 | 67.6
545 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND | WEST | 2012 | 30
546 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5
547 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2
548 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND | PANHANDLE | 2007 | 1
549 | Operational Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 14617.9
550 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PEAK_PCT_NC | % |  |  |  | 20
551
552 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
553 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
554 | CAMERON COUNTY WIND [CAMWIND_UNIT1] |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
555 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
556 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
557 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
558 | LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6
559 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
560 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
561 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
562 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
563 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
564 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
565 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
566 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
567 | Operational Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 2047.4
568 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 35
569
570 | Operational Wind Capacity Total (All Counties) |  | WIND_OPERATIONAL |  |  |  |  | 16665.3
571
572 | Operational Resources (Solar)
573 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
574 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2014 | 22
575 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
576 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
577 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 95
578 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
579 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
580 | BLUE WING 2 SOLAR |  | DG_ELEM_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
581 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
582 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
583 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CCS1 | DENTON | SOLAR | NORTH | 2015 | 2
584 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
585 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
586 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
587 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
588 | Operational Capacity Total (Solar) | [6 empty] | 287.7
589 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 5
590
591 | Available Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0
592
593 | Non-Synchronous Tie Resources
594 | EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600
595 | NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220
596 | EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30
597 | LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100
598 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150
599 | SHARYLAND RAILROAD TIE 2 |  | DC_R2 | HIDALGO |  | SOUTH |  | 150
600 | Non-Synchronous Ties Total | [6 empty] | 1250
601 | Non-Synchronous Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 246.4
602
603 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Water Rights
604 | COLORADO BEND II | 17INR0007 |  | WHARTON | GAS | SOUTH | 2017 | 0
605 | TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2019 | 0
606 | FGE TEXAS I PROJECT | 16INR0010 |  | MITCHELL | GAS | WEST | 2018 | 0
607 | ANTELOPE 1-3 IC (Switchable; Capacity = 168.0 MW) | 13INR0028 |  | HALE | GAS | WEST | 2016 | 0
608 | LA PALOMA ENERGY CENTER PROJECT | 16INR0004 |  | CAMERON | GAS | COASTAL | 2019 | 0
609 | PHR PEAKERS [BAC_CTG1-6] | 14INR0038 |  | GALVESTON | GAS | HOUSTON | 2016 | 390
610 | INDECK WHARTON ENERGY CENTER | 15INR0023 |  | WHARTON | GAS | SOUTH | 2019 | 0
611 | PINECREST ENERGY CENTER PROJECT | 16INR0006 |  | ANGELINA | GAS | NORTH | 2017 | 0
612 | RED GATE IC PLANT [REDGATE_AGR_A-D] | 14INR0040 |  | HIDALGO | GAS | SOUTH | 2016 | 225
613 | WOLF HOLLOW 2 | 17INR0009 |  | HOOD | GAS | NORTH | 2017 | 0
614 | FRIENDSWOOD G | 13INR0049 |  | HARRIS | GAS | HOUSTON | 2017 | 0
615 | BETHEL CAES PROJECT | 15INR0013 |  | ANDERSON | STORAGE | NORTH | 2018 | 0
616 | HALYARD HENDERSON | 16INR0045 |  | HENDERSON | GAS | NORTH | 2018 | 0
617 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS | SOUTH | 2018 | 0
618 | Planned Capacity Total (Coal, Gas & Storage) | [6 empty] | 615
619
620 | Planned Wind Resources with Executed SGIA
621 | ALBERCAS WIND | 15INR0049 |  | ZAPATA | WIND | SOUTH | 2016 | 0
622 | GUNSIGHT MOUNTAIN WIND | 08INR0018 |  | HOWARD | WIND | WEST | 2016 | 120
623 | MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | COASTAL | 2017 | 0
624 | LONGHORN WIND SOUTH | 14INR0023b |  | BRISCOE | WIND | PANHANDLE | 2017 | 0
625 | MARIAH WIND A | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2018 | 0
626 | MARIAH WIND B | 13INR0010b |  | PARMER | WIND | PANHANDLE | 2016 | 230.4
627 | MARIAH DEL SUR | 13INR0010c |  | PARMER | WIND | PANHANDLE | 2018 | 0
628 | RATTLESNAKE DEN WIND 2 | 13INR0020b |  | GLASSCOCK | WIND | WEST | 2018 | 0
629 | PATRIOT WIND (PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2017 | 0
630 | COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2018 | 0
631 | PAMPA WIND | 12INR0018 |  | GRAY | WIND | PANHANDLE | 2018 | 0
632 | WAKE WIND | 14INR0047 |  | DICKENS | WIND | PANHANDLE | 2016 | 257.3
633 | GRANDVIEW WIND 3 (CONWAY) | 13INR0005c |  | CARSON | WIND | PANHANDLE | 2016 | 0
634 | SCANDIA WIND DEF | 13INR0010def |  | PARMER | WIND | PANHANDLE | 2017 | 0
635 | PULLMAN ROAD WIND | 15INR0079 |  | RANDALL | WIND | PANHANDLE | 2018 | 0
636 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2016 | 0
637 | SALT FORK WIND | 14INR0062 |  | GRAY | WIND | PANHANDLE | 2016 | 174
638 | LOS VIENTOS IV WIND | 15INR0037 |  | STARR | WIND | SOUTH | 2016 | 200
639 | LOS VIENTOS V WIND [LV5_UNIT_1] | 15INR0021 |  | STARR | WIND | SOUTH | 2016 | 110
640 | PALO DURO WIND | 15INR0050 |  | DEAF SMITH | WIND | PANHANDLE | 2018 | 0
641 | CAPROCK WIND | 10INR0009 |  | CASTRO | WIND | PANHANDLE | 2017 | 0
642 | SAN ROMAN WIND | 14INR0013 |  | CAMERON | WIND-C | COASTAL | 2016 | 0
643 | TORRECILLAS WIND A | 14INR0045a |  | WEBB | WIND | SOUTH | 2017 | 0
644 | TORRECILLAS WIND B | 14INR0045b |  | WEBB | WIND | SOUTH | 2017 | 0
645 | CHANGING WINDS | 13INR0045 |  | CASTRO | WIND | PANHANDLE | 2017 | 0
646 | ELECTRA WIND | 16INR0062a |  | WILBARGER | WIND | WEST | 2016 | 230
647 | LOCKETT WIND FARM | 16INR0062b |  | WILBARGER | WIND | WEST | 2017 | 0
648 | HORSE CREEK WIND | 14INR0060 |  | HASKELL | WIND | WEST | 2016 | 230
649 | WILLOW SPRINGS WIND | 14INR0060b |  | HASKELL | WIND | WEST | 2017 | 0
650 | MUENSTER WIND | 15INR0085 |  | COOKE | WIND | NORTH | 2016 | 125.6
651 | HAPPY WHITEFACE WIND | 15INR0074 |  | DEAF SMITH | WIND | PANHANDLE | 2016 | 157
652 | CHAPMAN RANCH WIND I | 16INR0055 |  | NUECES | WIND-C | COASTAL | 2017 | 0
653 | HIDALGO & STARR WIND | 16INR0024 |  | HIDALGO | WIND | SOUTH | 2016 | 250
654 | BLANCO CANYON WIND (COTTON PLAINS) | 16INR0037 |  | FLOYD | WIND | PANHANDLE | 2016 | 0
655 | BLANCO CANYON WIND (OLD SETTLER) | 16INR0037b |  | FLOYD | WIND | PANHANDLE | 2017 | 0
656 | PUMPKIN FARM WIND | 16INR0037c |  | FLOYD | WIND | PANHANDLE | 2017 | 0
657 | ROCK SPRINGS VAL VERDE WIND | 11INR0082a |  | VAL VERDE | WIND | WEST | 2017 | 0
658 | MAGIC VALLEY WIND II (REDFISH 2A and 2B) | 14INR0041a |  | WILLACY | WIND-C | COASTAL | 2017 | 0
659 | SALT FORK WIND 2 | 16INR0082 |  | CARSON | WIND | PANHANDLE | 2017 | 0
660 | SANTA RITA WIND | 16INR0091 |  | REAGAN | WIND | WEST | 2017 | 0
661 | SWISHER WIND | 13INR0038 |  | SWISHER | WIND | PANHANDLE | 2017 | 0
662 | BUCKTHORN WIND 1 | 14INR0057 |  | ERATH | WIND | NORTH | 2016 | 96
663 | FLUVANNA RENEWABLE 1 | 13INR0056 |  | SCURRY | WIND | WEST | 2017 | 0
664 | RTS WIND | 16INR0087 |  | MCCULLOCH | WIND | SOUTH | 2016 | 0
665 | SILVER CANYON WIND A | 12INR0002a |  | BRISCOE | WIND | PANHANDLE | 2017 | 0
666 | LOGAN'S GAP WIND II | 15INR0082 |  | COMANCHE | WIND | NORTH | 2017 | 0
667 | CANADIAN BREAKS WIND | 13INR0026 |  | OLDHAM | WIND | PANHANDLE | 2017 | 0
668 | SALT FORK WIND EXPANSION | 16INR0121 |  | CARSON | WIND | PANHANDLE | 2017 | 0
669 | CHOCOLATE BAYOU | 16INR0074 |  | BRAZORIA | WIND-C | COASTAL | 2017 | 0
670 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND | PANHANDLE | 2016 | 500
671 | Planned Capacity Total (Wind) | [6 empty] | 2680.3
672
673 | Planned Wind Capacity Sub-total (Non-Coastal Counties) |  | WIND_PLANNED_NC |  |  |  |  | 2680.3
674 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PL_PEAK_PCT_NC | % |  |  |  | 20
675
676 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 0
677 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 35
678
679 | Planned Solar Resources with Executed SGIA
680 | FS BARILLA SOLAR 1B [HOVEY_UNIT2] | 12INR0059b |  | PECOS | SOLAR | WEST | 2016 | 7.4
681 | FS BARILLA SOLAR 2 | 12INR0059c |  | PECOS | SOLAR | WEST | 2017 | 0
682 | RE ROSEROCK SOLAR | 16INR0048 |  | PECOS | SOLAR | WEST | 2016 | 160
683 | OCI ALAMO 6 (WEST TEXAS) | 15INR0070_1 |  | PECOS | SOLAR | WEST | 2016 | 110
684 | OCI ALAMO 6 (WEST TEXAS PHASE II) | 15INR0070_1b |  | PECOS | SOLAR | WEST | 2016 | 50
685 | SE BUCKTHORN WESTEX SOLAR (RIGGINS SOLAR) | 15INR0045 |  | PECOS | SOLAR | WEST | 2017 | 0
686 | FS EAST PECOS SOLAR | 16INR0073 |  | PECOS | SOLAR | WEST | 2016 | 120
687 | OCI ALAMO 7 (PAINT CREEK) | 16INR0052 |  | HASKELL | SOLAR | WEST | 2016 | 106
688 | LC NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2016 | 201
689 | PECOS SOLAR POWER I | 15INR0059 |  | PECOS | SOLAR | WEST | 2019 | 0
690 | BNB LAMESA SOLAR | 16INR0023 |  | DAWSON | SOLAR | WEST | 2017 | 0
691 | BNB LAMESA SOLAR B | 16INR0023b |  | DAWSON | SOLAR | WEST | 2017 | 0
692 | CAPRICORN RIDGE SOLAR | 16INR0019 |  | COKE | SOLAR | WEST | 2017 | 0
693 | UPCO POWER 1 (SP-TX-12) | 16INR0065 |  | UPTON | SOLAR | WEST | 2017 | 0
694 | CASTLE GAP SOLAR 2 | 16INR0065a |  | UPTON | SOLAR | WEST | 2017 | 0
695 | SP-TX-12-PHASE B | 16INR0065b |  | UPTON | SOLAR | WEST | 2017 | 0
696 | SOLAIREHOLMAN 1 | 15INR0061 |  | BREWSTER | SOLAR | WEST | 2017 | 0
697 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2018 | 0
698 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2019 | 0
699 | RE MAPLEWOOD 2C SOLAR | 17INR0020c |  | PECOS | SOLAR | WEST | 2020 | 0
700 | RE MAPLEWOOD 2D SOLAR | 17INR0020d |  | PECOS | SOLAR | WEST | 2020 | 0
701 | Upton Solar | 16INR0114 |  | UPTON | SOLAR | WEST | 2017 | 0
702 | Planned Capacity Total (Solar) | [6 empty] | 754.4
703 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 5
704
705 | Seasonal Mothballed Resources
706 | MARTIN LAKE U2 (AS OF 10/1/2015) |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
707 | Total Seasonal Mothballed Capacity | [6 empty] | 820
708
709 | RMR Resources
710 | GREENS BAYOU STG U5 (available July-Sept. for both 2016 and 2017; June 2018) |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON |  | 371
711 | Total RMR Capacity | [6 empty] | 371
712
713 | Mothballed Resources
714 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1918 | 430
715 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1918 | 420
716 | LUFKIN BIOMASS (AS OF 7/6/2016) |  | LFBIO_UNIT1 | ANGELINA | BIOMASS | NORTH | 2012 | 45
717 | S R BERTRON CTG 2 (SINCE 5/15/2013) |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13
718 | S R BERTRON U1 (SINCE 5/15/2013) |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118
719 | S R BERTRON U2 (SINCE 5/15/2013) |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174
720 | S R BERTRON U3 (SINCE 5/22/2013) |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211
721 | S R BERTRON U4 (SINCE 5/22/2013) |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211
722 | Total Mothballed Capacity | [6 empty] | 1622
723
724 | Retiring Resources Unavailable to ERCOT (since last CDR)
725 | FRONTERA GENERATION CTG 1 (Not Available for ERCOT after 10/1/2016) |  | FRONTERA_FRONTEG1_RET | HIDALGO | GAS | SOUTH | 2016 | 170
726 | FRONTERA GENERATION CTG 2 (Not Available for ERCOT after 10/1/2016) |  | FRONTERA_FRONTEG2_RET | HIDALGO | GAS | SOUTH | 2016 | 170
727 | FRONTERA GENERATION STG (Not Available for ERCOT after 10/1/2016) |  | FRONTERA_FRONTEG3_RET | HIDALGO | GAS | SOUTH | 2016 | 184
728 | Total Retiring Capacity (since last CDR) | [6 empty] | 524

## Background
Release Date: September 1, 2016
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a one-in-ten-years loss-of-load event criteria on a probabilistic basis.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
In contrast to the Capacity, Demand and Reserves (CDR) report, which addresses the sufficiency of planning reserves on an annual basis as described above, the SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. Consequently, load reduction resources included in the CDR report, such as Emergency Response Service (ERS) and Load Resources that provide operating reserves (LRs), are excluded from the SARA.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur, and thus help fulfill the reporting requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). Several sensitivity analyses are developed by varying the value of certain parameters that affect resource adequacy. The variation in these parameters is based on historic values of these parameters or adjustments by any known or expected changes.