## Purpose
| 2017-01-01 | ERCOT Public
Mapping Document Related to NERC Standards - IRO-010-2 & TOP-003-3
Purpose
ERCOT ISO maintains this mapping document as required by North American Electric Reliability Corporation (NERC) Reliability Standards IRO-010-2 and TOP-003-3. This mapping document provides applicable NERC-registered entities with a list of existing Protocol and Operating Guide references that prescribe the data, specification and other relevant information required by ERCOT ISO to build and maintain its models to support Real-time Monitoring, Operational Analyses, and Real-time assessments. In the event of a conflict between the Protocols or Operating Guides and this mapping document, the Protocols and Operating Guides prevail.
NERC Definitions
Operational Planning Analysis (OPA) | An evaluation of projected system conditions to assess anticipated (pre-Contingency) and potential (post-Contingency) conditions for next-day operations. The evaluation shall reflect applicable inputs including, but not limited to, load forecasts; generation output levels; Interchange; known Protection System and Special Protection System status or degradation; Transmission outages; generator outages; Facility Ratings; and identified phase angle and equipment limitations. (Operational Planning Analysis may be provided through internal systems or through third-party services.)
Real-time Assessment (RTA) | An evaluation of system conditions using Real-time data to assess existing (pre-Contingency) and potential (post-Contingency) operating conditions. The assessment shall reflect applicable inputs including, but not limited to: load, generation output levels, known Protection System and Special Protection System status or degradation, Transmission outages, generator outages, Interchange, Facility Ratings, and identified phase angle and equipment limitations. (Real-time Assessment may be provided through internal systems or through third-party services.)
Revision and Distribution Process
This data specification mapping document and information document will be maintained by ERCOT ISO. Revisions will be distributed via market notice and posted to the ERCOT website.
Authors
Red = NRWG
Black/Grey = Initial Draft - ERCOT Staff
Orange = ERCOT Staff

## Data Requirements
Data Required for OPA/RTA & Real Time Monitoring
Section | Protocol Language | OPA | RTA | RTM | Periodicity | Deadline | Format & Security Protocol
3.1.4.4 | Management of Resource or Transmission Forced Outages or Maintenance Outages | Header | Header | Header
3.1.4.4(3) | For Maintenance Outages, the Resource Entity or QSE, as appropriate, or TSP shall notify ERCOT of any Resource or Transmission Facilities Maintenance Outage according to the Maintenance Outage Levels by updating the COP and Outage Scheduler. ERCOT shall coordinate the removal of facilities from service within the defined timeframes as specified by the TSP, QSE or Resource Entity in its notice to ERCOT. | X | X | X | Continually (3.1.2) | See 3.1.5.3 (1) | Outage Scheduler Digital Certificate
3.1.4.5 | Notice of Forced Outage or Unavoidable Extension of Planned or Maintenance Outage Due to Unforeseen Events | Header | Header | Header
3.1.4.5(1) | If a Planned or Maintenance Outage is not completed within the ERCOT-approved timeframe and the Transmission Facilities or Resources are in such a condition that they cannot be restored at the Outage schedule completion date, the requesting party shall submit to ERCOT a Forced Outage (unavoidable extension) form describing the extension of the Outage and providing a revised return date. | X | X | X | As it occurs | Before Planned or Maintenance outages ends | Outage Scheduler Digital Certificate
3.1.4.5(2) | Any Forced Outage that occurs in Real-Time must be entered into the Outage Scheduler if it is to remain an Outage for longer than two hours. | X | X | X | As it occurs | If outages remains longer than two hours | Outage Scheduler Digital Certificate
3.1.4.7 | Reporting of Forced Derates | Header
3.1.4.7 | The Resource Entity or its designee must enter Forced Derates that are expected to last more than 48 hours into the Outage Scheduler. | X | X | X | As it occurs | 48 hours | Outage Scheduler Digital Certificate
3.1.5.12 | Submittal Timeline for Transmission Facility Outage Requests | Header
3.1.5.12 | TSPs shall submit all requests for Planned Outages and Maintenance Outages or changes to existing approved Outages of Transmission Elements in the Network Operations Model to ERCOT no later than the minimum amount of time between the submittal of a request to ERCOT for approval of a proposed Outage and the scheduled start date of the proposed Outage, according to the following table (see table in protocols) | X |  |  | Continually | See table | Outage Scheduler Digital Certificate
3.1.6.2 | Resources Outage Plan | Header
3.1.6.2(1) | Resource Entity Outage requests shall include the following information: | X | X | X | As known | 45 days or immediately (3.1.6 (2)) | Outage Scheduler Digital Certificate
3.1.6.2(1)(a) | The primary and alternate phone number of the Resource Entity’s Single Point of Contact for Outage Coordination; | X | X | X | As known | 45 days or immediately | Outage Scheduler Digital Certificate
3.1.6.2(1)(b) | The Resource identified by the name in the Network Operations Model; | X | X | X | As known | 45 days or immediately | Outage Scheduler Digital Certificate
3.1.6.2(1)(c) | The net megawatts of capacity the Resource Entity anticipates will be available during the Outage (if any); | X | X | X | As known | 45 days or immediately | Outage Scheduler Digital Certificate
3.1.6.2(1)(d) | The estimated start and finish dates for each Planned and Maintenance Outage; | X | X | X | As known | 45 days or immediately | Outage Scheduler Digital Certificate
3.1.6.2(1)(e) | An estimate of the acceptable deviation in the Outage schedule (i.e., the earliest start date and the latest finish date for the Outage); and | X | X | X | As known | 45 days or immediately | Outage Scheduler Digital Certificate
3.1.6.2(1)(f) | The nature of work to be performed during the Outage. | X | X | X | As known | 45 days or immediately | Outage Scheduler Digital Certificate
3.1.6.11 | Outage Returning Early | Header
3.1.6.11(1) | A Resource that completes a Planned Outage early and wants to resume operation shall notify ERCOT of the early return prior to resuming service by making appropriate entries in the Current Operating Plan or Outage Scheduler if applicable as much in advance as practicable, but not later than at least two hours prior to beginning startup. Within two hours of receiving such request, ERCOT shall either: | X | X | X | As known | No later than 2 hours before start up | Outage Scheduler Digital Certificate
3.6 | Load Participation | Header | Header | Header
3.6.1 | Load Resource Participation | Header | Header | Header
3.6.1(1) | A Load Resource may participate by providing: | X | X | X | 2 seconds | Continuous | ICCP naming convention WAN
3.6.1(1)(a) | Ancillary Service: | X | X | X | 2 seconds | Continuous | ICCP naming convention WAN
3.6.1(1)(a)(i) | Regulation Up (Reg-Up) Service as a Controllable Load Resource capable of providing Primary Frequency Response; | X | X | X | 2 seconds | Continuous | ICCP naming convention WAN
3.6.1(1)(a)(ii) | Regulation Down (Reg-Down) Service as a Controllable Load Resource capable of providing Primary Frequency Response; | X | X | X | 2 seconds | Continuous | ICCP naming convention WAN
3.6.1(1)(a)(iii) | Responsive Reserve (RRS) Service as a Controllable Load Resource qualified for Security-Constrained Economic Dispatch (SCED) Dispatch and capable of providing Primary Frequency Response, or as a Load Resource controlled by high-set under-frequency relay; and | X | X | X | 2 seconds | Continuous | ICCP naming convention WAN
3.6.1(1)(a)(iv) | Non-Spinning Reserve (Non-Spin) Service as a Controllable Load Resource qualified for SCED Dispatch; | X | X | X | 2 seconds | Continuous | ICCP naming convention WAN
3.6.1(1)(b) | Energy in the form of Demand response from a Controllable Load Resource in Real-Time via SCED; | X | X | X | 2 seconds | Continuous | ICCP naming convention WAN
3.6.1(1)(c) | Emergency Response Service (ERS) for hours in which the Load Resource does not have an Ancillary Service Resource Responsibility; and | X | X | X | 2 seconds | Continuous | ICCP naming convention WAN
3.6.1(1)(d) | Voluntary Load response in Real-Time. | X | X | X | 2 seconds | Continuous | ICCP naming convention WAN
3.7 | Resource Parameters | Header | Header | Header
3.7(1) | A Resource Entity shall register All-Inclusive Resources pursuant to Planning Guide Section 6.8, Resource Registration Procedures. The Resource Parameters, listed in Section 3.7.1, Resource Parameter Criteria, are a subset of Resource Registration data defined in the Resource Registration Glossary. | X | X | X | As needed | Model ready date | RARF (series of spreadsheets) MIS/Digital Certificate
3.7.1.1 | Generation Resource Parameters | Header | Header | Header
| Generation Resource Parameters that may be modified, with documented reason for change, by the QSE for immediate use upon ERCOT validation include: | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(a) | Normal Ramp Rate curve; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(b) | Emergency Ramp Rate curve; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(c) | Minimum On-Line time; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(d) | Minimum Off-Line time; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(e) | Maximum On-Line time; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(f) | Maximum daily starts; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(g) | Maximum weekly starts; | X | X | X |  |  | EIP XML or other external app Digital Certificate
(h) | Maximum weekly energy; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(i) | Hot start time; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(j) | Intermediate start time; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(k) | Cold start time; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(l) | Hot to intermediate time; and | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
(m) | Intermediate to cold time. | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2 | Load Resource Parameters | Header | Header | Header
3.7.1.2(1) | Resource Parameters that may be modified, with documented reason for change, by the QSE for immediate use upon ERCOT validation, which may be adjusted to reflect Distribution Losses in accordance with Section 8.1.1.2, General Capacity Testing Requirements, include the following for each of its Load Resources that is a non-Controllable Load Resource: | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(1)(a) | Maximum interruption time; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(1)(b) | Maximum daily deployments; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(1)(c) | Maximum weekly deployments; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(1)(d) | Maximum weekly energy; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(1)(e) | Minimum notice time; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(1)(f) | Minimum interruption time; and | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(1)(g) | Minimum restoration time. | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(2) | Resource Parameters that may be modified, with documented reason for change, by the QSE for immediate use upon ERCOT validation, which may be adjusted to reflect Distribution Losses in accordance with Section 8.1.1.2, include the following for each of its Controllable Load Resources, including Aggregate Load Resources (ALRs): | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(2)(a) | Normal Ramp Rate curve; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(2)(b) | Emergency Ramp Rate curve; | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(2)(c) | Maximum deployment time; and | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.7.1.2(2)(d) | Maximum weekly energy. | X | X | X | As needed | As needed | EIP XML or other external app Digital Certificate
3.9.1 | Current Operating Plan (COP) Criteria | Header
3.9.1(2) | Each QSE that represents a Resource shall update its COP reflecting changes in availability of any Resource as soon as reasonably practicable, but in no event later than 60 minutes after the event that caused the change. | X |  |  | Various |  | EIP XML or other external app Digital Certificate
3.9.1(5) | A COP must include the following for each Resource represented by the QSE: | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(a) | The name of the Resource; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b) | The expected Resource Status: | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i) | Select one of the following for Generation Resources synchronized to the ERCOT System that best describes the Resource’s status. Unless otherwise provided below, these Resource Statuses are to be used for COP and/or Real-Time telemetry purposes, as appropriate. | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(A) | ONRUC – On-Line and the hour is a RUC-Committed Hour; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(B) | ONREG – On-Line Resource with Energy Offer Curve providing Regulation Service; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(C) | ON – On-Line Resource with Energy Offer Curve or Off-Line Quick Start Generation Resource (QSGR) available for Security-Constrained Economic Dispatch (SCED) Dispatch; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
|  | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(D) | ONDSR – On-Line Dynamically Scheduled Resource (DSR); | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(E) | ONOS – On-Line Resource with Output Schedule; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(F) | ONOSREG – On-Line Resource with Output Schedule providing Regulation Service; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(G) | ONDSRREG – On-Line DSR providing Regulation Service; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(H) | FRRSUP – Available for Dispatch of Fast Responding Regulation Service (FRRS). This Resource Status is only to be used for Real-Time telemetry purposes; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(I) | ONTEST – On-Line blocked from SCED for operations testing (while ONTEST, a Generation Resource may be shown on Outage in the Outage Scheduler); | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(J) | ONEMR – On-Line EMR (available for commitment or dispatch only for ERCOT-declared Emergency Conditions; the QSE may appropriately set LSL and High Sustained Limit (HSL) to reflect operating limits); | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(K) | ONRR – On-Line as a synchronous condenser (hydro) providing Responsive Reserve (RRS) but unavailable for Dispatch by SCED and available for commitment by RUC; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(L) | ONOPTOUT – On-Line and the hour is a RUC Buy-Back Hour; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(M) | SHUTDOWN – The Resource is On-Line and in a shutdown sequence, and has no Ancillary Service Obligations other than Off-Line Non-Spinning Reserve (Non-Spin) which the Resource will provide following the shutdown. This Resource Status is only to be used for Real-Time telemetry purposes; and | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(i)(N) | STARTUP – The Resource is On-Line and in a start-up sequence and has no Ancillary Service Obligations. This Resource Status is only to be used for Real-Time telemetry purposes. | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(ii) | Select one of the following for Off-Line Generation Resources not synchronized to the ERCOT System that best describes the Resource’s status. These Resource Statuses are to be used for COP and/or Real-Time telemetry purposes, as appropriate. | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(ii)(A) | OUT – Off-Line and unavailable; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(ii)(B) | OFFNS – Off-Line but reserved for Non-Spin; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(ii)(C) | OFF – Off-Line but available for commitment in the Day-Ahead Market (DAM) and RUC; and | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(ii)(D) | EMR – Available for commitment only for ERCOT-declared Emergency Condition events; the QSE may appropriately set LSL and HSL to reflect operating limits; and | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(iii) | Select one of the following for Load Resources. Unless otherwise provided below, these Resource Statuses are to be used for COP and/or Real-Time telemetry purposes. | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(iii)(A) | ONRGL – Available for Dispatch of Regulation Service by Load Frequency Control (LFC) and, for any remaining Dispatchable capacity, by SCED with an Real-Time Market (RTM) Energy Bid; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(iii)(B) | FRRSUP – Available for Dispatch of FRRS by LFC and not Dispatchable by SCED. This Resource Status is only to be used for Real-Time telemetry purposes; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(iii)(C) | FRRSDN - Available for Dispatch of FRRS by LFC and not Dispatchable by SCED. This Resource Status is only to be used for Real-Time telemetry purposes; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(iii)(D) | ONCLR – Available for Dispatch as a Controllable Load Resource by SCED with an RTM Energy Bid; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(iii)(E) | ONRL – Available for Dispatch of RRS Service, excluding Controllable Load Resources; and | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(b)(iii)(F) | OUTL – Not available; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(c) | The HSL; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(c)(i) | For Load Resources other than Controllable Load Resources, the HSL should equal the expected power consumption; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(d) | The LSL; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(d)(i) | For Load Resources other than Controllable Load Resources, the LSL should equal the expected Low Power Consumption (LPC); | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(e) | The High Emergency Limit (HEL); | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(f) | The Low Emergency Limit (LEL); and | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(g) | Ancillary Service Resource Responsibility capacity in MW for: | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(g)(i) | Regulation Up (Reg-Up); | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(g)(ii) | Regulation Down (Reg-Down); | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(g)(iii) | RRS Service; and | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(5)(g)(iv) | Non-Spin. | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.9.1(6) | For Combined Cycle Generation Resources, the above items are required for each operating configuration. In each hour only one Combined Cycle Generation Resource in a Combined Cycle Train may be assigned one of the On-Line Resource Status codes described above. | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Digital Certificate
3.10.1 | Time Line for Network Operations Model Changes | Header
3.10.1(3) | TSPs and Resource Entities shall submit Network Operations Model updates at least three months prior to the physical equipment change. ERCOT shall update the Network Operations Model according to the following table (see table in protocols) | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.1 | Transmission Lines | Header | Header | Header
3.10.7.1.1(2) | For each of its transmission lines operated as part of the ERCOT Transmission Grid, each TSP and if applicable, Resource Entity, shall provide ERCOT with the following information consistent with the ratings methodology prescribed in the ERCOT Operating Guides: | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.1(2)(a) | Equipment owner(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.1(2)(b) | Equipment operator(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.1(2)(c) | Transmission Element name; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.1(2)(d) | Line impedance; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.1(2)(e) | Normal Rating, Emergency Rating, 15-Minute Rating, and Conductor/Transformer 2-Hour Rating; and | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.1(2)(f) | Other data necessary to model Transmission Element(s). | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.1(4) | The TSP and Resource Entity may implement protective relay and control systems and set values appropriate to de-energize faulted equipment and meet the TSP and Resource Entity obligations for public or employee safety, and when necessary to prevent in-service or premature equipment failure consistent with Good Utility Practice and accepted industry standards. The TSP and Resource Entity shall include those limits when providing ERCOT with ratings or proposed transfer limits. | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.2 | Transmission Buses | Header | Header | Header
3.10.7.1.2(2) | Each TSP and if applicable, Resource Entity, shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.2(2)(a) | Equipment owner(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.2(2)(b) | Equipment operator(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.2(2)(c) | The Transmission Element name; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.2(2)(d) | The substation name; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.2(2)(e) | A description of all transmission circuits that may be connected through breakers or switches; and | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.2(2)(f) | Other data necessary to model Transmission Element(s). | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3 | Transmission Breakers and Switches | Header | Header | Header
3.10.7.1.3(2) | Each TSP and Resource Entity shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3(2)(a) | Equipment owner(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3(2)(b) | Equipment operator(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3(2)(c) | The Transmission Element name; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3(2)(d) | The substation name; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3(2)(e) | Connectivity; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3(2)(f) | Normal status; and | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3(2)(g) | Breaker phase angle limits (Draft NPRR) | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3(2)(g) | Other data necessary to model Transmission Element(s). | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3(3) | ERCOT shall develop methods to accurately model changes in transmission line loading resulting from Load rollover schemes transferring more than ten MW. This may include modeling distribution circuit breakers, dead line sensing, or other methods that signal when the Load should be transferred from one transmission line to another transmission line. ERCOT may employ heuristic rule sets for all manual Load transfers and for automated transfers where feasible. ERCOT application software is required to model the effects of automatic or manual schemes in the field transfer Load under line outage conditions. Each TSP and as applicable, Resource Entity, shall define the Load rollover schemes under Section 3.10.7.2, Modeling of Resources and Transmission Loads, and furnish this information to ERCOT. Transmission field (right-of-way) switches must be connected to a named Electrical Bus and be included in the Network Operations Model. | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.4 | Transmission and Generation Resource Step-Up Transformers | Header | Header | Header
3.10.7.1.4(3) | Each TSP and Resource Entity shall provide ERCOT with information to accurately describe each transformer in the Network Operations Model including any tertiary Load as required by ERCOT. Each TSP and Resource Entity shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.4(3)(a) | Equipment owner(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.4(3)(b) | Equipment operator(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.4(3)(c) | The Transmission Element name; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.4(3)(d) | The substation name; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.4(3)(e) | Winding ratings; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.4(3)(f) | Connectivity; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.4(3)(g) | Transformer parameters, including all tap parameters; and | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.4(3)(h) | Other data necessary to model Transmission Element(s). | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.5 | Reactors, Capacitors, and other Reactive Controlled Sources | Header | Header | Header
3.10.7.1.5(2) | Each Market Participant shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.5(2)(a) | Equipment owner(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.5(2)(b) | Equipment operator(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.5(2)(c) | The Transmission Element name; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.5(2)(d) | The substation name; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.5(2)(e) | Voltage or time switched on; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.5(2)(f) | Voltage or time switched off; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.5(2)(g) | Associated switching device name; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.5(2)(h) | Connectivity; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.5(2)(i) | Nominal voltage and associated capacitance or reactance; and | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.2 | Modeling of Resources and Transmission Loads | Header | Header | Header
3.10.7.2(4) | ERCOT shall create a DC Tie Resource to represent an equivalent generation injection to represent the flow into the ERCOT Transmission Grid from operation of DC Ties. The actual injection flow on the DC Tie from telemetry provided by the facility owner(s) is the DC Tie Resource output. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
3.10.7.3 | Modeling of Private Use Networks | Header | Header | Header
ERCOT shall create and use network models describing Private Use Networks according to the following:
3.10.7.3(1) | A Generation Entity with a Resource located within a Private Use Network shall provide data to ERCOT, for use in the Network Operations Model, for each of its individual generating unit(s) located within the Private Use Network in accordance with Section 3.3.2.1, Information to Be Provided to ERCOT, if it meets any one of the following criteria: | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.3(1)(a) | Contains a generator greater than ten MW and is registered with the PUCT according to P.U.C. Subst. R. 25.109, Registration of Power Generation Companies and Self-Generators, as a power generation company; or | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.3(1)(b) | Is part of a Private Use Network which contains more than one connection to the ERCOT Transmission Grid; or | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.3(1)(c) | Contains generation registered to provide Ancillary Services. | X | X | X | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.3(2) | A Generation Entity with a generator greater than ten MW located within a Private Use Network which does not meet any of the criteria of item (1) above shall provide to ERCOT annually, or more often upon change, the following information for ERCOT’s use in the Network Operations Model, for each of its individual generating unit(s) located within the Private Use Network:
3.10.7.3(2)(a) | Equipment owner(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | RARF (series of spreadsheets) MIS/Digital Certificate
3.10.7.3(2)(b) | Equipment operator(s); | X | X | X | As needed | At least 3 months prior to the physical equipment changes | RARF (series of spreadsheets) MIS/Digital Certificate
3.10.7.3(2)(c) | TSP substation name connecting the Private Use Network to the ERCOT System; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | RARF (series of spreadsheets) MIS/Digital Certificate
3.10.7.3(2)(d) | At the request of ERCOT, a description of Transmission Elements within the Private Use Network that may be connected through breakers or switches; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | RARF (series of spreadsheets) MIS/Digital Certificate
3.10.7.3(2)(e) | Net energy delivery metering, as required by ERCOT, to and from a the Private Use Network and the ERCOT System at the POI with the TSP; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | RARF (series of spreadsheets) MIS/Digital Certificate
3.10.7.3(2)(f) | For each individual generator located within the Private Use Network, the gross capacity in MW and its reactive capability curve; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | RARF (series of spreadsheets) MIS/Digital Certificate
3.10.7.3(2)(g) | Maximum and minimum reasonability limits of the Load located within the Private Use Network; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | RARF (series of spreadsheets) MIS/Digital Certificate
3.10.7.3(2)(h) | Outage schedule for each generation unit located within the Private Use Network, updated as changes occur from the annually submitted information; and | X | X | X | As needed | At least 3 months prior to the physical equipment changes | RARF (series of spreadsheets) MIS/Digital Certificate
3.10.7.5.2 | Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows | Header | Header | Header
3.10.7.5.2(1) | Each TSP or QSE shall provide telemetry of voltages, flows, and Loads on any modeled Transmission Element to the extent such may be required to estimate all transmission Load withdrawals and generation injections to and from the ERCOT Transmission Grid using the SE and as needed to achieve the State Estimator Standards with consideration given to the economic implications of inaccurate LMP results versus the cost to remedy. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
3.10.8.1 | Dynamic Ratings Delivered via ICCP | Header | Header | Header
3.10.8.1(1) | The TSP shall supply the following, via ICCP, updated at least every ten minutes: | X | X | X | At least every ten minutes | Ten minutes | ICCP Naming Convention WAN
3.10.8.1(1)(a) | Normal Rating; and | X | X | X |  |  | ICCP Naming Convention WAN
3.10.8.1(1)(b) | Optionally Emergency Rating and/or 15-Minute Rating (required when Emergency Rating is provided). | X | X | X |  |  | ICCP Naming Convention WAN
3.10.8.5 | Transmission Service Provider Responsibilities Related to Dynamic Ratings | Header | Header | Header
3.10.8.5 | Each TSP shall: | X | X | X
3.10.8.5(a) | Provide ERCOT with tables of ratings for different ambient temperatures for Transmission Elements, as requested by ERCOT. | X | X | X | As needed | Within 2 months | NOMCR Digital Certificate/Citrix
3.10.8.5(b) | Submit within two months a temperature adjusted rating table when a request is received from ERCOT unless multiple requests are made by ERCOT within the two-month period or unusual circumstances prevent the request from being accommodated in a timely fashion. Such circumstances must be explained to ERCOT in writing and must be posted by ERCOT on the MIS Secure Area within five Business Days of receipt. | X | X | X | As needed | Within 2 months | NOMCR Digital Certificate/Citrix
3.10.8.5(c) | Provide Real-Time temperatures for each Weather Zone in which the TSP has existing dynamically rated transmission equipment, or alternatively provide rating updates for each temperature-adjusted line rating updated at least once every ten minutes. | X | X | X | At least every ten minutes | Within 2 months | ICCP Naming Convention WAN
3.13 | Renewable Production Potential Forecasts | Header | Header | Header
3.13(1) | ERCOT shall produce forecasts of Renewable Production Potential (RPP) for Wind-powered Generation Resources (WGRs) and PhotoVoltaic Generation Resources (PVGRs) to be used as an input into the Day-Ahead Reliability Unit Commitment (DRUC) and Hour-Ahead Reliability Unit Commitment (HRUC). ERCOT shall produce the forecasts using information provided by WGR/PVGR Entities, meteorological information, and Supervisory Control and Data Acquisition (SCADA). WGR and PVGR Entities shall install telemetry at their respective Resources and transmit the ERCOT-specified site-specific meteorological information to ERCOT. WGR and PVGR Entities shall also provide detailed equipment status at the WGR/PVGR facility as specified by ERCOT to support the RPP forecast. ERCOT shall post forecasts for each WGR and PVGR to the Qualified Scheduling Entities (QSEs) representing WGRs and/or PVGRs on the Market Information System (MIS) Certified Area. QSEs shall use the ERCOT-provided forecasts for WGRs/PVGRs throughout the Day-Ahead and Operating Day for applicable markets and Reliability Unit Commitments (RUCs). Similar requirements for run-of-the-river hydro must be developed as needed. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
3.15 | Voltage Support | Header | Header | Header
3.15(12) | All WGRs must provide a Real-Time SCADA point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid. WGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following: | X | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
3.15(12)(a) | The number of wind turbines that are not able to communicate and whose status is unknown; and | X | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
3.15(12)(b) | The number of wind turbines out of service and not available for operation. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
3.15(13) | All PhotoVoltaic Generation Resources (PVGRs) must provide a Real-Time SCADA point that communicates to ERCOT the capacity of PhotoVoltaic (PV) equipment that is available for real power and/or Reactive Power injection into the ERCOT Transmission Grid. PVGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following: | X | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
3.15(13)(a) | The capacity of PV equipment that is not able to communicate and whose status is unknown; and | X | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
3.15(13)(b) | The capacity of PV equipment that is out of service and not available for operation. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
3.15.3 (4) | Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is going On-Line or Off-Line or the QSE determines a need to operate in manual mode in the event of an Emergency Condition at the generating plant. Each QSE shall send to ERCOT via telemetry, the AVR and Power System Stabilizer (PSS) status of each Generation Resource providing VSS. For AVRs, an “On” status will indicate the AVR is on and set to regulate the Resource’s terminal voltage in the voltage control mode, and an “Off” status will indicate the AVR is off or in a manual mode. Each QSE shall monitor the status of their regulators and stabilizers, and shall report abnormal status changes to ERCOT. |  | X | X | 2 10 seconds | Continuous | ICCP Naming Convention WAN
4.2.2 | Wind-Powered Generation Resource Production Potential | Header | Header | Header
4.2.2(1) | ERCOT shall produce and update hourly a Short-Term Wind Power Forecast (STWPF) that provides a rolling 168-hour hourly forecast of wind production potential for each Wind-powered Generation Resource (WGR). ERCOT shall produce and update an hourly Total ERCOT Wind Power Forecast (TEWPF) providing a probability distribution of the hourly production potential from all wind-power in ERCOT for each of the next 168 hours. Each Generation Entity that owns a WGR shall install and telemeter to ERCOT the site-specific meteorological information that ERCOT determines is necessary to produce the STWPF and TEWPF forecasts. ERCOT shall establish procedures specifying the accuracy requirements of WGR meteorological information telemetry. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
4.4.4 | DC Tie Schedules | Header | Header | Header
4.4.4(7) | A QSE exporting from ERCOT and/or importing to ERCOT through a DC Tie shall: | X | X | X
4.4.4(7)(b) | Submit e-Tags for all proposed transactions; and | X | X | X | As needed | 15 minutes before the schedule ramps | OATI Internet
6.4.2.5 | DSR Load |  | Header | Header
6.4.2.5(3)(a) | All power signals for DSR Load must be sent to ERCOT in Real-Time by telemetry; and |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.4.5 | Incremental and Decremental Energy Offer Curves | Header | Header | Header
6.4.6 | Resource Status |  | Header | Header
6.4.6(1) | ERCOT shall use the telemetered Resource Status for all applications requiring status of Resources during the Operating Hour, including SCED and Load Frequency Control (LFC). QSEs shall provide ERCOT with accurate telemetry of the current capability of each Resource including the Resource Status, Ramp Rates, HSL, and LSL. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.1 | Changes in Resource Status |  | Header | Header
6.5.5.1(1) | Each QSE shall notify ERCOT of a change in Resource Status via telemetry and through changes in the Current Operating Plan (COP) as soon as practicable following the change. | X | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2 | Operational Data Requirements |  | Header | Header
6.5.5.2(2)(a) | Net real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered gross real power and conversion constants determined by the Resource Entity and provided to ERCOT through the Resource Registration process. Net real power represents the actual generation of a Resource for all real power dispatch purposes, including use in Security-Constrained Economic Dispatch (SCED), determination of the High Ancillary Service Limit (HASL), High Dispatch Limit (HDL), Low Dispatch Limit (LDL) and Low Ancillary Service Limit (LASL), and is consistent with telemetered HSL, LSL and Non-Frequency Responsive Capacity (NFRC); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(b) | Gross real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered real power, which may include Supervisory Control and Data Acquisition (SCADA) metering, and conversions constants determined by the Resource Entity and provided to ERCOT through the Resource Registration process; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(c) | Gross Reactive Power (in Megavolt-Amperes reactive (MVAr)); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(d) | Net Reactive Power (in MVAr); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(e) | Power to standby transformers serving plant auxiliary Load; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(f) | Status of switching devices in the plant switchyard not monitored by the TSP or DSP affecting flows on the ERCOT Transmission Grid; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(h) | Generation Resource breaker and switch status; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(i) | HSL (Combined Cycle Generation Resources) shall: |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(i)(i) | Submit the HSL of the current operating configuration; and |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(i)(ii) | When providing RRS, update the HSL as needed, to be consistent with Resource performance limitations of RRS provision; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(j) | NFRC currently available (unloaded) and included in the HSL of the Combined Cycle Generation Resource’s current configuration; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(k) | High Emergency Limit (HEL), under Section 6.5.9.2, Failure of the SCED Process; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(l) | Low Emergency Limit (LEL), under Section 6.5.9.2; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(m) | LSL; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(n) | Configuration identification for Combined Cycle Generation Resources; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(o) | Ancillary Service Schedule for each quantity of RRS and Non-Spin which is equal to the Ancillary Service Resource Responsibility minus the amount of Ancillary Service deployment; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(o)(i) | For On-line Non-Spin, Ancillary Service Schedule shall be set to zero; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(o)(ii) | For Off-Line Non-Spin and for On-Line Non-Spin using Off-Line power augmentation technology the Ancillary Service Schedule shall equal the Non-Spin obligation and then shall be set to zero within 20 minutes following Non-Spin deployment; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(p) | Ancillary Service Resource Responsibility for each quantity of Regulation Up (Reg-Up), Regulation Down (Reg-Down), RRS and Non-Spin. The sum of Ancillary Service Resource Responsibility for all Resources in a QSE is equal to the Ancillary Service Supply Responsibility for that QSE; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(q) | Reg-Up and Reg-Down Services participation factors represent how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s). The Reg-Up and Reg-Down Services participation factors for a Resource providing Fast Responding Regulation Up Service (FRRS-Up) or Fast Responding Regulation Down Service (FRRS-Down) shall be zero; and |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(2)(r) | The designated Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources shall provide Real-Time telemetry for items (a), (b), (c), (d), (e), (g), and (h) above, PSS and AVR status for the total Generation Resource in addition to the Split Generation Resource the Master QSE represents. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(3) | For each Intermittent Renewable Resource (IRR), the QSE shall set the HSL equal to the current net output capability of the facility. The net output capability should consider the net real power of the IRR generation equipment, IRR generation equipment availability, weather conditions, and whether the IRR net output is being affected by compliance with a SCED Dispatch Instruction. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(4) | For each Aggregate Generation Resource (AGR), the QSE shall telemeter the number of its generators online. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5) | A QSE representing a Load Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time data to ERCOT for each Load Resource and ERCOT shall make the data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to the Load Resource’s host TSP or DSP at the TSP’s or DSP’s expense. The Load Resource’s net real power consumption, Low Power Consumption (LPC) and Maximum Power Consumption (MPC) shall be telemetered to ERCOT using a positive (+) sign convention:
6.5.5.2(5)(a) | Load Resource net real power consumption (in MW); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5)(c) | Load Resource breaker status; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5)(d) | LPC (in MW); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5)(e) | MPC (in MW); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5) (f) | Ancillary Service Schedule (in MW) for each quantity of RRS and Non-Spin, which is equal to the Ancillary Service Resource Responsibility minus the amount of Ancillary Service deployment; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5)(g) | Ancillary Service Resource Responsibility (in MW) for each quantity of Reg-Up and Reg-Down for Controllable Load Resources, and RRS and Non-Spin for all Load Resources; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5)(h) | The status of the high-set under-frequency relay, if required for qualification; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5)(i) | For a Controllable Load Resource providing Non-Spin, the Scheduled Power Consumption that represents zero Ancillary Service deployments; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5)(j) | For a single-site Controllable Load Resource with registered maximum Demand response capacity of ten MW or greater, net Reactive Power (in MVAr); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5)(k) | Resource Status (Resource Status shall be ONRL if high-set under-frequency relay is active); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5)(l) | Reg-Up and Reg-Down services participation factor, which represents how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s). The Reg-Up and Reg-Down services participation factors for a Resource providing FRRS-Up or FRRS-Down shall be zero; and |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(5)(m) | For a Controllable Load Resource providing Non-Spin, the “Scheduled Power Consumption Plus Two Hours,” representing the QSE’s forecast of the Controllable Load Resource’s instantaneous power consumption for a point two hours in the future. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(7)(a) | Raise Block Status and Lower Block Status are telemetry points used in transient unit conditions to communicate to ERCOT that a Resource’s ability to adjust its output has been unexpectedly impaired. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(7)(e) | The Resource limits and Ancillary Service telemetry shall be updated as soon as practicable. Raise Block Status and Lower Block Status will then be disabled. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(9) | Each QSE shall report the current configuration of combined-cycle Resources that it represents to ERCOT. The telemetered Resource Status for a Combined Cycle Generation Resource may only be assigned a Resource Status of OFFNS if no generation units within that Combined Cycle Generation Resource are On-Line. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.5.2(10) | A QSE representing Combined Cycle Generation Resources shall provide ERCOT with the possible operating configurations for each power block with accompanying limits. Combined Cycle Train power augmentation methods may be included as part of one or more of the registered Combined Cycle Generation Resource configurations. Power augmentation methods may include: | X | X | X | various | As needed | RARF (series of spreadsheets) MIS/Digital Certificate
6.5.7.1.7 | Real-Time Weather and Dynamic Rating Processor |  | Header | Header
6.5.7.1.7(1) | The Dynamic Rating Processor provides Dynamic Ratings using the processes described in Section 3.10.8, Dynamic Ratings, for all transmission lines and transformer elements with Dynamic Ratings designated by the TSPs. ERCOT shall obtain Real-Time weather data, where available, from multiple locations and provide it to the Dynamic Rating Processor. Weather conditions must include ambient temperature and may include wind speed when available. ERCOT shall post summaries of dynamically adjusted Transmission Element limits on the MIS Secure Area in a form that allows Market Participants to directly upload Real-Time data into the Common Information Model (CIM). |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.12 | Resource Limits |  | Header | Header
6.5.7.1.12(2)(b)(i) | Normal Ramp Rate based on the values telemetered by the QSE to ERCOT; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.12(2)(b)(ii) | Emergency Ramp Rate based on the values telemetered by the QSE to ERCOT; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.12(2)(b)(iii) | SURAMP, which represents the ability of a Load Resource to decrease consumption in SCED; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.12(2)(b)(iv) | SDRAMP, which represents the ability of a Load Resource to increase consumption in SCED; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.13 | Data Inputs and Outputs for the Real-Time Sequence and SCED |  | Header | Header
6.5.7.1.13(1)(a)(i) | Transmission Electrical Bus voltages; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.13(1)(a)(ii) | MW and MVAr pairs for all transmission lines, transformers, and reactors; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.13(1)(a)(iii) | Actual breaker and switch status for all modeled devices; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.13(1)(a)(iv) | Tap position for auto-transformers; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.13(1)(c)(ii) | Data from QSEs: |  | header | header
6.5.7.1.13(1)(a)(ii)(A) | Generator Step-Up (GSU) transformers tap position; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.13(1)(a)(ii)(B) | Resource HSL (from telemetry); and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.13(1)(a)(ii)(C) | Resource LSL (from telemetry); and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.1.13(1)(d) | Real-Time weather, from WGRs, and where available from TSPs or other sources. ERCOT may elect to obtain other sources of weather data and may utilize such information to calculate the dynamic limit of any Transmission Element. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.6.1 | LFC Process Description
6.5.7.6.2.3 | Non-Spinning Reserve Service Deployment |  | Header | Header
6.5.7.6.2.3(7) | For DSRs providing Non-Spin, on deployment of Non-Spin, the DSR’s QSE shall adjust its Resource Output Schedule to reflect the amount of deployment. For non-DSRs with Output Schedules providing Non-Spin, on deployment of Non-Spin, ERCOT shall adjust the Resource Output Schedule for the remainder of the Operating Period to reflect the amount of deployment. ERCOT shall notify the QSEs representing the non-DSR of the adjustment through the MIS Certified Area. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention WAN
6.5.7.7 | Voltage Support Service | Header | Header | Header
6.5.9.5 | Block Load Transfers between ERCOT and Non-ERCOT Control Areas |  | Header | Header
6.5.9.5(h) | SCADA telemetry on switching devices at BLT points that are deemed necessary by ERCOT to be modeled in the Network Operations Model must be provided by the TSP registering the BLT. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention WAN
Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability.
Section | Protocol Language |  |  |  | Periodicity | Deadline | Format & Security Protocol
OG 6.2.4 | Protective Relay System Failure Response | Header | Header | Header
OG 6.2.4(4) | The affected QSE or TO shall immediately notify the ERCOT Shift Supervisor via phone call and initiate prompt corrective action. These corrective actions are to address reliability issues for the systems that the QSE and TO monitor and/or operate. |  |  |  | As soon as reasonably practicable |  | Phone
OG 6.2.4(7) | The affected QSE and TO shall promptly notify the ERCOT Shift Supervisor via phone call of the return to service of the previously identified protective relay systems. |  |  |  | As soon as reasonably practicable |  | Phone
OG 11.2 | Special Protection System | Header | Header | Header
OG 11(2)(e) | When an SPS is removed from service, the SPS owner or its Designated Agent shall immediately notify ERCOT;… |  |  |  | As soon as reasonably practicable |  | Phone
OG 11 (2) (f) | When an SPS is returned to service, the SPS owner or its Designated Agent shall immediately notify ERCOT… |  |  |  | As soon as reasonably practicable |  | Phone

## Revision History
Date | Version | Description and Reason for Change | Author(s)
2017-01-01 | 1 | First draft | ERCOT Staff

## Requirement Mapping
NERC Standard IRO-010-2 & TOP-003-3 Requirements |  | Response
IRO-010-2 R1 | The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments. The data specification shall include but not be limited to: | ERCOT ISO's data specification is outlined in the ERCOT Protocols and Operating Guides. The Protocol and Operating Guide references are also provided in the "Data Requirements" tab of this mapping document.
TOP-003-3 R1 | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments. The data specification shall include, but not be limited to:
TOP-003-3 R2 | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real‐time monitoring. The data specification shall include, but not be limited to
IRO-010-2 R1.1 | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real‐time monitoring, and Realtime Assessments including non‐BES data and external network data, as deemed necessary by the Reliability Coordinator. | ERCOT ISO's data specification is outlined in the ERCOT Protocols and Operating Guides. The Protocol and Operating Guide references are provided in the "Data Requirements" tab of this document.
TOP-003-3 R1.1 | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real‐time monitoring, and Realtime Assessments including non‐BES data and external network data as deemed necessary by the Transmission Operator.
TOP-003-3 R2.1 | A list of data and information needed by the Balancing Authority to support its analysis functions and Real‐time monitoring
IRO-010-2 R1.2 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability | The provisions for owners of Protection System and Special Protection System to provide ERCOT ISO with status or degradation are in Operating Guide Sections 6.2.4, Protective Relay System Failure Response & 11.2, Special Protection System and also referenced in row xx of the "Data Requirements" tab of this mapping document.
TOP-003-3 R1.2 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability.
TOP-003-3 R2.2 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability
IRO-010-2 R1.3 | A periodicity for providing data. | The periodicity for providing data is outlined in the Protocols and Operating Guides
TOP-003-3 R1.3 | A periodicity for providing data.
TOP-003-3 R2.3 | A periodicity for providing data
IRO-010-2 R1.4 | The deadline by which the respondent is to provide the indicated data. | The deadline by which the respondent is to provide the data indicated is outlined in the Protocols and Operating Guides
TOP-003-3 R1.4 | The deadline by which the respondent is to provide the indicated data
TOP-003-3 R2.4 | The deadline by which the respondent is to provide the indicated data
IRO-010-2 R2 | The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Realtime monitoring, And Real‐time Assessments. | ERCOT ISO distributes the Protocols and Operating Guides as required by Section 21 and Section 2 of the Operating Guides. Additionally, ERCOT ISO distributes this mapping document via a market notice in accordance with the revision process prescribed in the Purpose tab of this document.
TOP-003-3 R3 | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Realtime monitoring, and Real‐time Assessment
TOP-003-3 R4 | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real‐time monitoring
IRO-010-2 R3 | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load‐Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: | ERCOT ISO is the single RC and BA in the ERCOT Interconnection
TOP-003-3 R5 | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load‐Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: | Insert CFR language and details about how we will comply with LCC-developed data specs.
IRO-010-2 R3.1 | A mutually agreeable format | Since ERCOT ISO's data specification is outlined in the ERCOT Protocols and Operating Guides, the respective revision request process is considered the mutually agreeable format
TOP-003-3 R5.1 | A mutually agreeable format
IRO-010-2 R3.2 | A mutually agreeable process for resolving data conflicts | See details of NOGRR162
TOP-003-3 R5.2 | A mutually agreeable process for resolving data conflicts
IRO-010-2 R3.3 | A mutually agreeable security protocol | Since ERCOT ISO's data specification is outlined in the ERCOT Protocols and Operating Guides, the respective revision request process and associated impact analysis prescribe the mutually agreeable security protocol by which specified data will be submitted
TOP-003-3 R5.3 | A mutually agreeable security protocol