## Slide 1: Panhandle Export Update
 | Panhandle Export Limit (MW) based on WSCR
Previous Limit | 3702(1)
Updated Limit | 4013
Panhandle Wind Generation Capacity: 5271 MW
Include 2nd circuit (Alibates-AJ Swope-Windmill-Ogallala-Tule Canyon) and two 175 MVAR synchronous condensers
The updated limit will be used in the 2016 RTP economic analysis
(1). http://www.ercot.com/content/wcm/key_documents_lists/76860/Panhandle_RPG_ERCOT_review_10202015.pdf