## Slide 1
GIC Model – Transformer DC Resistances
Important Considerations
September 26, 2016

## Slide 2: Disclaimer
  This presentation is being provided for informational purposes only and does not purport to be comprehensive. Neither CenterPoint Energy, Inc., together with its subsidiaries and affiliates (the “Company”), nor its employees or representatives, make any representation or warranty (express or implied) relating to this information. By reviewing this presentation, you agree that the Company will not have any liability related to this information or any omissions or misstatements contained herein. You are encouraged to perform your own independent evaluation and analysis.

## Slide 3: DC Resistance in Autotransformers
  DC Resistance data values presented in various ways
    H, X, Y
    H1-H0, H2-H0, H3-H0, X1-X0, X2-X0, X3-X0, Y1-Y2, Y2-Y3, Y3-Y1
    H-X, X-0, Y
    H1-X1, X1-H0X0, Y1-Y2, etc.
    HV, XV, YV
    Series, common, LV
  Diagrams within the datasheets should supersede all notational norms
  For the model, values represent common, series, and tertiary resistance values, not high, low, and tertiary winding values for autotransformers (per section 7.2.4 in PSS/E v34 POM)

## Slide 4: Other Considerations
  Measurement Temperature & Reporting Temperature
    May only be provided at measurement temperature
    May only be provided at reported temperature (85°, 75°, etc.)
    May have both measurement temperature and reported temperature
    Need to convert to 75° value per NERC Application Guide
        **Above eqn. in IEEE C57.152-2013
  Resistances provided in per phase versus total
    Average phase values given for use in submission
    Must divide total resistance values by 3 to obtain per phase values
  Resistances provided for tap positions
    Per NERC Application Guide, values are to be for the neutral tap
Rs= resistance at Ts
Rm=measured resistance
Ts=desired temp. (C°)
Tm= measurement temp. (C°)
Tk= 234.5 C° copper, 225 C° aluminum

## Slide 5: Autotransformer Winding Diagram
YNa0d1