## Slide 1
AEPSC and Oncor Barrilla Junction Transmission Project – ERCOT Independent Review
TAC
September 29, 2016

## Slide 2: Background
The oil and gas development in the Permian Basin in West Texas has introduced significant load growth in the Barrilla Junction area.
The load along the Barrilla Junction/Solstice to Permian Basin 138 kV transmission line is committed to reach 150 MW by 2020.
AEP submitted project proposal to the Regional Planning Group (RPG) in December 2015. During the independent review process, AEP submitted additional study to address the dynamic need of the area.

## Slide 3: Study Region

## Slide 4: ERCOT Independent Review
ERCOT confirmed reliability criteria violations without the project
  Summer peak N-1 (NERC P1, P2-1 and P7) voltage and thermal violations by 2021
  Dynamic Studies indicated reliability criteria violations according to ERCOT Planning Guide Section 4.1.1.5, Transient Voltage Response Criteria.
ERCOT evaluated three options
  All three options could meet the reliability criteria.
  Option B was the least cost and required no new Right of Way.

## Slide 5: ERCOT Recommendation
ERCOT will recommend the Board endorse Option B to address the reliability need in the study region:
  Rebuild the existing Barrilla Junction/Solstice to Permian Basin AEP-TNC/Oncor 138 kV transmission line (approximately 54 miles).
  Install one new 100/-50 MVAR SVC at Hackberry Tap/Lotebush.
The total cost estimate for Option B is approximately $77 million.
  The costs estimate assume that the Barrilla Junction/Solstice to Permian Basin 138 kV line will be rebuilt “energized”.
Estimated in service date is June 2019.

## Slide 6
Questions?