## Slide 1
TNMP Line 69H Rebuild and Conversion Project – ERCOT Independent Review
TAC
September 29, 2016

## Slide 2: Background
The TNMP West Texas North (WTN) System, which is mainly served by Line 69H, 69D and 69E, is experiencing steady load growth with a significant amount of the forecasted load from facilities tapped from Line 69H.
By 2022, the total coincident peak load forecast in the WTN system will reach 254 MW, which will cause reliability criteria violations, and the majority of the criteria violations are located on Line 69H.
TNMP submitted the Line 69H Rebuild and Conversion project for the Regional Planning Group review in March 2016.

## Slide 3: Study Region

## Slide 4: ERCOT Independent Review
ERCOT confirmed reliability criteria violations without the project
  Summer peak N-1 (NERC P1) caused voltage and thermal violations by 2018
ERCOT evaluated three options
  All involved rebuilding the existing Line 69H to 138 kV standards and the addition of static capacitor bank
  Two options (Option 1 and Option 3) meet the reliability criteria
  Option 1 provides the benefit of reducing the loading on other transmission lines in the TNMP WTN system

## Slide 5: ERCOT Recommendation
ERCOT will recommend the Board endorse Option 1 to address the reliability need in the study region:
  Rebuild Line 69H from IH-20 to Wickett to 138kV standards with 1926 ACSR conductor (~39 miles)
  Rebuild three existing substations (Pyote, Worsham and Collie Field Tap) along Line 69H to 138kV standards.
  Connect to IH-20 38kV substation
  Build new Wickett 138kV ring substation
  Install Wickett 138/69kV autotransformer
  Build Wickett to Oncor Wolf 138kV transmission line with 1926 ACSR conductor (~6.0 miles)
The total cost estimate for Option 1 is approximately $50.6 million
Estimated in-service date is fall 2019

## Slide 6
Questions?