## Slide 1: Planning Geomagnetic Disturbance Task Force (PGDTF) Update to the ROS
October 6, 2016
Michael Juricek
PGDTF Chairman
<number>
10/6/2016 ROS Meeting

## Slide 2
TPL-007-1 Standard Status Update
On January 21, 2015, NERC filed a petition seeking FERC approval of Proposed Reliability Standard TPL-007-1, Transmission System Planned Performance for Geomagnetic Disturbance Events.
On February 26, 2015, Foundation for Resilient Societies, Inc. Initiated a Level 2 Appeal which NERC is Processing.
On May 14, 2015, FERC Issued NOPR Proposing to Approve NERC TPL-007-1 and Directing NERC as Follows.
  Modify the Benchmark GMD Event Definition and Transformer Thermal Impact Study Requirements.
  Require Installation of Monitoring Equipment.
  Establish Specific Deadlines for the Development of Corrective Action Plans and the Completion of Plan Activities.
On July 27, 2015, NERC provided comments in response to the FERC NOPR.
<number>
Michael Juricek - 10/6/2016 ROS Meeting
Notes: <number>

## Slide 3
TPL-007-1 Standard Status Update
On March 1, 2016, a FERC technical conference was convened to discuss the issues in the NOPR.
NERC filed supplemental information on August 17, 2015, April 28, 2016 and June 28, 2016.
On September 22, 2016, FERC issued Order No. 830 approving Reliability Standard TPL-007-1 (Transmission System Planned Performance for Geomagnetic Disturbance Events). TPL-007-1 establishes requirements for certain registered entities to assess the vulnerability of their transmission systems to GMDs, which occur when the sun ejects charged particles that interact with and cause changes in the earth’s magnetic fields. Applicable entities that do not meet certain performance requirements, based on the results of their vulnerability assessments, must develop a plan to achieve the performance requirements.
Michael Juricek - 10/6/2016 ROS Meeting
<number>
Notes: <number>

## Slide 4
TPL-007-1 Standard Status Update
In addition, the Commission directs NERC to develop modifications to Reliability Standard TPL-007-1.
  To modify the benchmark GMD event definition set forth in Attachment 1 of Reliability Standard TPL-007-1, as it pertains to the required GMD Vulnerability Assessments and transformer thermal impact assessments, so that the definition is not based solely on spatially-averaged data;
  To require the collection of necessary GIC monitoring and magnetometer data and to make such data publicly available; and
  To include a one-year deadline for the development of corrective action plans; two-year deadline to complete mitigation actions involving non-hardware mitigation and four-year deadline to complete mitigation actions involving hardware mitigation.
FERC also directs NERC to submit the revisions within 18 months of the effective date the Final Rule. Additionally, the Commission also directs NERC to submit a work plan and (GMD research work plan) within 6 months of the effective date of the Final Rule, and subsequently, one or more informational filings that address specific GMD-related research areas.
Michael Juricek - 10/6/2016 ROS Meeting
<number>
Notes: <number>

## Slide 5: Implementation Plan
Date of 01/2017
Approval
60 days after Publication in the Federal Register
18 Months 07/2018
R2
System Models
48 Months 01/2021
R6
Thermal Assessment
6 Months 07/2017
R1
Identify Responsibilities
24 Months 01/2019
R5
GIC Flow Information
60 Months 01/2022
R3, R4, and R7
Performance Criteria
GMD Assessment
Corrective Action Plan
Michael Juricek - 10/6/2016 ROS Meeting
<number>

## Slide 6
TPL-007-1 Summary
R1 requires to identify the individual and joint responsibilities of the Planning Coordinator (ERCOT) and Transmission Planners in ERCOT’s area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment.
R2 requires to maintain System models and GIC System (DC) models of the responsible entity’s planning area for performing the studies needed to complete GMD Vulnerability Assessment
    Guidance for developing the GIC System model is provided in the GIC Application Guide developed by the NERC GMD Task Force and available at: http://www.nerc.com/comm/PC/Geomagnetic%20Disturbance%20Task%20Force%20GMDTF%202013/GIC%20Application%20Guide%202013_approved.pdf
R3 requires to have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1.
Applicability: ERCOT and Transmission Planners Responsible for R1, R2 and R3
Michael Juricek - 10/6/2016 ROS Meeting
<number>
Notes: <number>

## Slide 7
R4 requires a GMD Vulnerability Assessment of the system to determine its ability to withstand a Benchmark GMD Event without causing voltage collapse
  Assessment performed once every five years
R5 requires to provide GIC flow information to be used for the transformer thermal impact assessment specified in R6 to each TO and GO that owns an applicable BES power transformer in the planning area.
  Additional guidance is available in the Transformer Thermal Impact Assessment white paper: http://www.nerc.com/pa/Stand/Pages/Project-2013-03-Geomagnetic-Disturbance-Mitigation.aspx
  Applicability: ERCOT Responsible for R4 and R5
  With Support from Transmission Planners
TPL-007-1 Summary
Michael Juricek - 10/6/2016 ROS Meeting
<number>
Notes: <number>

## Slide 8
TPL-007-1 Summary
R6 requires a Transformer Thermal Impact Assessment to ensure high-side, wye grounded BES transformers connected at 200kV or higher will not overheat based on the benchmark event
    Applies to transformers where effective GIC identified in GIC studies 75 A per phase or greater (not 75 A continuous). Effective 75 A per phase is a conservative screening criterion
    Approaches for conducting the assessment are presented in the Transformer Thermal Impact Assessment white paper posted on the project page http://www.nerc.com/pa/Stand/Pages/Project-2013-03-Geomagnetic-Disturbance-Mitigation.aspx
    Performed once every five years with GMD Vulnerability Assessment
    Applicability: Generator Owners and Transmission Owners Responsible for R6
Michael Juricek - 10/6/2016 ROS Meeting
<number>
Notes: <number>

## Slide 9
TPL-007-1 Summary
R7 requires to develop a Corrective Action Plan addressing how the performance requirements will be met if through the GMD Vulnerability Assessment responsible entity determined that System does not meet the performance requirements of Table 1.
  Assessment performed once every five years with GMD Vulnerability Assessment
  Corrective Action Plans as defined in the NERC Glossary of Terms: A list of actions and an associated timetable for implementation to remedy a specific problem.
  Applicability: ERCOT and Transmission Planners Responsible for R7
Michael Juricek - 10/6/2016 ROS Meeting
<number>
Notes: <number>

## Slide 10
The NERC GMD TF has developed general guidelines for performing GMD Vulnerability Assessments that are described in TPL-007-1 :
  NERC Geomagnetic Disturbance Planning Guide
  NERC GIC Application Guide
  NERC Transformer Thermal Impact Assessment White Paper
Existing Guidance for Performing
GMD Analysis
Michael Juricek - 10/6/2016 ROS Meeting
<number>
Notes: <number>

## Slide 11: September 28, 2016 Meeting
Discussed FERC’s Order
Discussed Data Requirements for GIC System Model.
Reviewed List of Questions for GIC Software Vendor.
Discussed Target Date for TSPs’ Data for GIC System Model.
Discussed Next Activities.
Michael Juricek – 10/6/2016 ROS Meeting
<number>

## Slide 12: Next Activities for PGDTF
Develop for Documentation GMD Planning Responsibilities (R1).
Create GIC System Model for Geomagnetic Disturbance (GMD) Vulnerability Assessment (R2).
Develop Schedule for Meeting Requirements in the Standard.
Hold Meeting in October 2016
Michael Juricek - 10/6/2016 ROS Meeting
<number>

## Slide 13: Questions and Answers
<number>
Michael Juricek - 10/6/2016 ROS Meeting