| NPRR Number | 747 | NPRR Title | Revision of Voltage Control Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | October 11, 2016 |  |
| Action |  | Approved |  |
| Timeline |  | Normal |  |
| Effective Date |  | Upon implementation of Nodal Operating Guide Revision Request (NOGRR) 150, Alignment with NPRR747, Revision of Voltage Control Requirements. |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Protocol Sections Requiring Revision |  | 2.1, Definitions 3.15, Voltage Support 3.15.3, QSE Responsibilities Related to Voltage Support 6.5.7.7, Voltage Support Service |  |
| Related Documents Requiring Revision/ Related Revision Requests |  | NOGRR150 |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) proposes new definitions related to Voltage Profiles, defines various Entities’ responsibilities related to Voltage Support, and also clarifies that the interconnecting Transmission Service Provider (TSP) (or its designated agent) may modify a Generation Resource’s Voltage Set Point. This NPRR addresses issues raised at the April 8, 2015 Voltage Workshop. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This NPRR reduces operational risk by clarifying roles and responsibilities related to voltage instructions as well as introducing definitions that acknowledge that Voltage Set Points may vary from the Seasonal Voltage Profiles due to varying system conditions. These definitions also establish concepts that will be expounded upon in future NPRRs and NOGRRs to continue to address issues identified in the April 2015 Voltage Workshop. |  |
| Credit Work Group Review |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR747 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |
| PRS Decision |  | On 12/10/15, PRS unanimously voted to table NPRR747 and refer the issue to WMS and ROS. All Market Segments were present for the vote. On 6/16/16, PRS voted to recommend approval of NPRR747 as amended by the 4/21/16 ERCOT comments. There was one abstention from the Consumer Market Segment. All Market Segments were present for the vote. On 7/14/16, PRS unanimously voted to endorse and forward to TAC the 6/16/16 PRS Report and Impact Analysis for NPRR747. All Market Segments were present for the vote. |  |
| Summary of PRS Discussion |  | On 12/10/15, there was no discussion. On 6/16/16, there was no discussion. On 7/14/16, there was no discussion. |  |
| TAC Decision |  | On 7/28/16, TAC unanimously voted to recommend approval of NPRR747 as recommended by PRS in the 7/14/16 PRS Report. All Market Segments were present for the vote. |  |
| Summary of TAC Discussion |  | On 7/28/16, there was no discussion. |  |
| ERCOT Opinion |  | ERCOT supports approval of NPRR747. |  |
| Board Decision |  | On 8/9/16, the ERCOT Board took no action on NPRR747. On 10/11/16, the ERCOT Board approved NPRR747 as recommended by TAC in the 7/28/16 TAC Report with an ERCOT Board action effective date of 8/9/16. |  |

| Sponsor |  |
| --- | --- |
| Name | Stephen Solis |
| E-mail Address | Stephen.solis@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6772 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| CenterPoint Energy 120415 | Provided clarifying edits to the language. |
| Calpine 120415 | Recommended PRS table NPRR747 and refer the issue to ROS, and provided additional revisions to the definition of “Voltage Set Point” and Section 6.5.7.7. |
| Exelon 120715 | Supported NPRR747 as submitted. |
| Oncor 120815 | Provided additional revisions to the 12/4/15 Calpine comments. |
| ROS 011116 | Requested NPRR747 be tabled for review by the Operations Working Group (OWG). |
| NRG 011316 | Proposed numerous language changes including changes to the reactive capability requirement and point of contact for Ancillary Service deployment instructions. |
| ERCOT 011916 | Proposed numerous language changes including changes to the issuance of Voltage Set Point instructions, communication of the instructions, and the definition of Voltage Set Point. |
| Exelon 012016 | Proposed clarifying edits in Section 3.15.3 related to Power System Stabilizer (PSS) status. |
| GDF Suez 020116 | Proposed additional clarifying edits to Section 3.15. |
| Luminant 020316 | Proposed additional clarifying edits to Section 6.5.5.7. |
| AEP 021116 | Proposed edits relating to communication paths between Entities. |
| Austin Energy 021716 | Proposed additional edits to the definition of Voltage Profile and to clarify Automatic Voltage Regulator (AVR) requirements in Sections 2.1 and 3.15.3. |
| STEC 022316 | Expressed support for the intent of NPRR747. |
| ERCOT 042116 | Proposed language changes to remove any proposed changes to Voltage Set Point instructions from NPRR747 for inclusion in a future NPRR. |
| WMS 060916 | Endorsed the 4/21/16 ERCOT comments. |
| ROS 060916 | Endorsed the 4/21/16 ERCOT comments. |

Market Rules Notes

Please note that the baseline Protocol language in the following sections has been updated to reflect the incorporation of the following NPRR(s) into the Protocols:

- NPRR588, Clarifications for PV Generation Resources (unboxed 2/10/16)

  - Section 3.15

- NPRR705, Provides Consistency for References to the End Date of the Generation Interconnection Process (incorporated 1/1/16)

  - Section 3.15

Please also note the following NPRR(s) also propose(s) revisions to the following section(s):

- NPRR776, Voltage Set Point Communication

  - Section 6.5.7.7

Proposed Protocol Language Revision

## 2.1	DEFINITIONS

- Voltage Profile

The set of normally desired Voltage Set Points for those Generation Resources specified in paragraph (2) of Section 3.15, Voltage Support, in the ERCOT System for

- Voltage Set Point

The voltage that a Generation Resource is required to maintain at its Point of Interconnection and that is initially communicated via the Voltage Profile but may be modified by a Real-Time instruction from ERCOT, the interconnecting TSP, or that TSP’s agent.

Automatic Voltage Regulator (AVR)

A device on a Generation Resource or a control system at the Facility of a Generation Resource used to automatically control the voltage to an established Voltage Set Point.

3.15	Voltage Support

(1)	ERCOT, in coordination with the Transmission Service Providers (TSPs), shall establish and update, as necessary, the ERCOT System Voltage Profile and shall post it on the Market Information System (MIS) Secure Area.  ERCOT, the interconnecting TSP, or that TSP’s agent, may modify the Voltage Set Point described in the Voltage Profile based on current system conditions.

(2)	All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than 20 MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than 20 MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

(3)	Each Generation Resource required to provide VSS shall comply with the following Reactive Power Requirements:

(a)	An over-excited (lagging or producing) power factor capability of 0.95 or less determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and the Generation Resource’s set point in the Voltage Profile measured at the POI;

(b)	An under-excited (leading or absorbing) power factor capability of 0.95 or less, determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and the Generation Resource’s set point in the Voltage Profile measured at the POI;

(c)	Reactive Power capability shall be available at all MW output levels and may be met through a combination of the Generation Resource’s Unit Reactive Limit (URL), which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAr capable devices.  This Reactive Power profile is depicted graphically as a rectangle.  For Intermittent Renewable Resources (IRRs), the Reactive Power requirements shall be available at all MW output levels at or above 10% of the IRR’s nameplate capacity.  When an IRR is operating below 10% of its nameplate capacity and is unable to support voltage at the POI, ERCOT may require an IRR to disconnect from the ERCOT System for purposes of maintaining reliability; and

(d)	As part of the technical Resource testing requirements prior to the Resource Commissioning Date, all Generation Resources must conduct an engineering study, or demonstrate through performance testing, compliance with the Reactive Power capability requirements of this Section.  Any study or testing results must be accepted by ERCOT prior to the Resource Commissioning Date.

(4)	Wind-powered Generation Resources (WGRs) that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before December 1, 2009 (“Existing Non-Exempt WGRs”), must be capable of producing a defined quantity of Reactive Power to maintain a set point in the Voltage Profile established by ERCOT in accordance with the Reactive Power requirements established in paragraph (3) above, except in the circumstances described in paragraph (a) below.

(a)	Existing Non-Exempt WGRs whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above must conduct an engineering study using the Summer/Fall 2010 on-peak/off-peak Voltage Profiles, or conduct performance testing to determine their actual Reactive Power capability.  Any study or testing results must be accepted by ERCOT.  The Reactive Power requirements applicable to these Existing Non-Exempt WGRs will be the greater of: the leading and lagging Reactive Power capabilities established by the Existing Non-Exempt WGR’s engineering study or testing results; or Reactive Power proportional to the real power output of the Existing Non-Exempt WGR (this Reactive Power profile is depicted graphically as a triangle) sufficient to provide an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the WGR’s set point in the Voltage Profile established by ERCOT, and both measured at the POI.

(i)	Existing Non-Exempt WGRs shall submit the engineering study results or testing results to ERCOT no later than five Business Days after its completion.

(ii)	Existing Non-Exempt WGRs shall update any and all Resource Registration data regarding their Reactive Power capability documented by the engineering study results or testing results.

(iii)	If the Existing Non-Exempt WGR’s engineering study results or testing results indicate that the WGR is not able to provide Reactive Power capability that meets the triangle profile described in paragraph (4)(a) above, then the Existing Non-Exempt WGR will take steps necessary to meet that Reactive Power requirement depicted graphically as a triangle by a date mutually agreed upon by the Existing Non-Exempt WGR and ERCOT.  The Existing Non-Exempt WGR may meet the Reactive Power requirement through a combination of the WGR’s URL and/or automatically switchable static VAr capable devices and/or dynamic VAr capable devices.  No later than five Business Days after completion of the steps to meet that Reactive Power requirement, the Existing Non-Exempt WGR will update any and all Resource Registration data regarding its Reactive Power and provide written notice to ERCOT that it has completed the steps necessary to meet its Reactive Power requirement.

(iv)	For purposes of measuring future compliance with Reactive Power requirements for Existing Non-Exempt WGRs, results from performance testing or the Summer/Fall 2010 on-peak/off-peak Voltage Profiles utilized in the Existing Non-Exempt WGR’s engineering study shall be the basis for measuring compliance, even if the Voltage Profiles provided to the Existing Non-Exempt WGR are revised for other purposes.

(b)	Existing Non-Exempt WGRs whose current design allows them to meet the Reactive Power requirements established in paragraph (3) above (depicted graphically as a rectangle) shall continue to comply with that requirement.  ERCOT, with cause, may request that these Existing Non-Exempt WGRs provide further evidence, including an engineering study, or performance testing, to confirm accuracy of Resource Registration data supporting their Reactive Power capability.

(5)	Qualified Renewable Generation Resources (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(6)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the Operating Guides.

(7)	For purposes of meeting the Reactive Power requirements in paragraphs (3) through (6) above, multiple generation units including IRRs shall, at a Generation Entity’s option, be treated as a single Generation Resource if the units are connected to the same transmission bus.

(8)	Generation Entities may submit to ERCOT specific proposals to meet the Reactive Power requirements established in paragraph (3) above by employing a combination of the URL and added VAr capability, provided that the added VAr capability shall be automatically switchable static and/or dynamic VAr devices.  A Generation Resource and TSP may enter into an agreement in which the proposed static VAr devices can be switchable using Supervisory Control and Data Acquisition (SCADA).  ERCOT may, at its sole discretion, either approve or deny a specific proposal, provided that in either case, ERCOT shall provide the submitter an explanation of its decision.

(9)	A Generation Resource and TSP may enter into an agreement in which the Generation Resource compensates the TSP to provide VSS to meet the Reactive Power requirements of paragraph (3) above in part or in whole.  The TSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (3).

(10)	Unless specifically approved by ERCOT, no unit equipment replacement or modification at a Generation Resource shall reduce the capability of the unit below the Reactive Power requirements that applied prior to the replacement or modification.

(11)	Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent.

(12)	All WGRs must provide a Real-Time SCADA point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  WGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following:

(a)	The number of wind turbines that are not able to communicate and whose status is unknown; and

(b)	The number of wind turbines out of service and not available for operation.

(13)	All PhotoVoltaic Generation Resources (PVGRs) must provide a Real-Time SCADA point that communicates to ERCOT the capacity of PhotoVoltaic (PV) equipment that is available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  PVGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following:

(a)	The capacity of PV equipment that is not able to communicate and whose status is unknown; and

(b)	The capacity of PV equipment that is out of service and not available for operation.

(14)	For the purpose of complying with the Reactive Power requirements under this Section 3.15, Reactive Power losses that occur on privately-owned transmission lines behind the POI may be compensated by automatically switchable static VAr capable devices.

- 3.15.3	Generation Resource Requirements Related to Voltage Support

(1)	Generation Resources required to provide VSS shall have and maintain Reactive Power capability at least equal to the Reactive Power capability requirements specified in these Protocols and the ERCOT Operating Guides.

(2)	Generation Resources providing VSS shall be compliant with the ERCOT Operating Guides for response to transient voltage disturbance.

(3)	Generation Resources providing VSS must meet technical requirements specified in Section 8.1.1.1, Ancillary Service Qualification and Testing, and the performance standards specified in Section 8.1.1, QSE Ancillary Service Performance Standards.

(4)	Each Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the automatic voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is telemetering its Resource Status as STARTUP, SHUTDOWN, or ONTEST, or the QSE determines a need to operate in manual mode in the event of an Emergency Condition at the generating plant.

(5)	Each Generation Resource providing VSS shall maintain the Voltage Set Point established by ERCOT, the interconnecting TSP, or the TSP’s agent, subject to the Generation Resource’s operating characteristic limits, voltage limits, and within tolerances identified in paragraph (4) of Operating Guide Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource Requirements.

(6)	The reactive capability required must be maintained at all times that the Generation Resource is On-Line.

(7)	Each QSE shall send to ERCOT, via telemetry, the AVR and Power System Stabilizer (PSS) status for each of its Generation Resources providing VSS.  For AVRs, an “On” status will indicate the AVR is on and set to regulate the Resource’s terminal voltage in the voltage control mode, and an “Off” status will indicate the AVR is off or in a manual mode.  For PSS, an “On” status will indicate the service is enabled and ready for service, and an “Off” status will indicate it is off or out of service.  Each QSE shall monitor the status of its Generation Resources’ regulators and stabilizers, and shall report status changes to ERCOT.

(8)	Each Resource Entity shall provide information related to the tuning parameters, local or inter-area, of any PSS installed at a Generation Resource.

6.5.7.7	Voltage Support Service

(1)	ERCOT shall coordinate with TSPs the creation and maintenance of Voltage Profiles as described in Section 3.15, Voltage Support.

(2)	ERCOT, or TSPs designated by ERCOT, shall instruct QSEs having a Generation Resource required to provide Voltage Support Service (VSS) to make adjustments for voltage support within the Unit Reactive Limit (URL) provided by the QSE to ERCOT.  If ERCOT determines that a Generation Resource should be instructed to provide additional MVAr beyond its URL or that a Generation Resource’s real power output should be decreased to allow the Generation Resource to provide additional Reactive Power beyond the URL, ERCOT shall issue a Resource-specific Dispatch Instruction requiring any change in Reactive Power and/or real power output, except that ERCOT may not require a Generation Resource to exceed its excitation limits.

(3)	ERCOT and TSPs shall develop procedures for the operation of transmission-controlled reactive Resources in order to minimize the dependence on generation-supplied reactive Resources.  For Generation Resources required to provide VSS, GSU transformer tap settings must be managed to maximize the use of the ERCOT System for all Market Participants while maintaining adequate reliability.

(4)	Each TSP, under ERCOT’s direction, is responsible for monitoring and ensuring that all Generation Resources required to provide VSS have their dynamic reactive capability deployed in approximate proportion to their respective capability requirements.

(5)	Each Generation Resource required to provide VSS shall follow its Voltage Set Point as directed by ERCOT, the interconnecting TSP, or the TSP’s agent, within the operating Reactive Power capability of the Generation Resource.