## Slide 1
QMWG Update on SCR788
Addition of Integral ACE Feedback to GTBD Calculation
Operations Planning
ERCOT
October 14th, 2016

## Slide 2: SCR788 Addition of Integral ACE Feedback to GTBD Calculation
This SCR updates the formula used by the Resource Limit Calculator to calculate the Generation To Be Dispatched (GTBD) value. The update will include the addition of Area Control Error (ACE) Integral times a configurable factor that captures the long-term Dispatch trend to help minimize GTBD oscillations from one Security-Constrained Economic Dispatch (SCED) interval to the next. The analysis further shows that having an Integral ACE feedback would reduce the amount of manual Time Error corrections performed.
Integral ACE is calculated from Raw ACE by integrating the raw ACE value over a configurable amount of time (X seconds) and adding it to the previous 4 second
Integral ACE, as shown below:
Integral ACE (current 4 sec) = Integral ACE(last 4 sec) + [(Raw ACE(Current 4 sec)*(Current Time – Last AGC run time))/X]
In general, Integral ACE provides a good indication of which direction ACE has been trending.

## Slide 3: SCR788 Modifications
1. Add the K5 configurable factor together with the Integral ACE calculated in the Energy Management System (EMS).
2. The Maximum Integral ACE Feedback, Maximum Regulation Deployed Feedback and K5 factor should all be tunable parameters.
  Generation To Be Dispatched = Total Gen + K1*10*System Load Frequency Bias + K2*[(net non-conforming Load) – (net filtered non-conforming Load)] + K3*5*PLRR + K4*Regulation Deployed + K5*ACE Integral
    |ACE Integral| ≤ Max Integral ACE Feedback
    |Regulation Deployed| ≤ Max Regulation Deployed Feedback
3. Ability to integrate the Raw ACE over X seconds for use in the ACE Integral equation, where the variable X can be configured.

## Slide 4: SCR788 Current Timeline
Currently in ERCOT project phase
Planned to be released to production in early December (R6)
  12/8/16
Once in production, ACE Integral will be slowly be incorporated into GTBD
  Configurable factors are still under evaluation and will be set to slowly integrate ACE Integral into GTBD.

## Slide 5: Questions?
Thank you!