## Responsibilities
TPL-007-1 |  | Responsibilities Between ERCOT, TPs, GOs and TOs DRAFT 03/13/2015
Requirement |  | ERCOT Responsibility | TP Responsibility | TO Responsibility | GO Responsibility | Violation Risk Factor | Time Horizon | Rationale | Clarifications | Comments
R1 | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). | Yes | Yes |  |  | Lower | Long-term Planning | Planning entities may determine that the most effective approach to conduct a GMD Vulnerability Assessment is through a regional planning organization. |  | Proposal - Sponsor new PGRR ( Add Section 3.1.1.5 Geomagnetic Disturbance Assessment Process ) ERCOT responsible for drafting PGRR for compliance with R1. Generally, PGRR will propose responsibilities as follows: ERCOT responsible for maintaining models per PGDTF Guides for compliance with R2. ERCOT responsible for performing planning study for compliance with R4. ERCOT responsible for providing maximum and times series GIC flows per R5. TSP and Resource Entities responsible for performing transformer thermal impact assessment per R6. R1 requires identification of resposibilities for preperation of models and performing studies; therefore R3 & R7 not involved.
R2 | Each responsible entity, as determined in R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | Yes | Yes |  |  | High | Long-term Planning | A GMD Vulnerability Assessment requires a GIC System model to calculate GIC flow which is used to determine transformer Reactive Power absorption and transformer thermal response. Guidance for developing the GIC System model is provided in the GIC Application Guide developed by the NERC GMD Task Force and available at: http://www.nerc.com/comm/PC/Geomagnetic%20Disturbance%20Task%20Force%20GMDTF%202013/GIC%20Application%20Guide%202013_approved.pdf | The GIC System model is 1) used in conducting steady state power flow analysis that accounts for the Reactive Power absorption of power transformer(s) due to GIC in the System; 2) includes all power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV; 3) used to calculate GIC flow in the network. The projected System condition for GMD planning may include adjustments to the System that are executable in response to space weather information. These adjustments could include, for example, recalling or postponing maintenance outages. | • ERCOT coordinates, builds and maintains the models in accordance with updated Planning Guide and newly created PGDTF Procedure Manual. • Each TP provides data necessary for building and maintaining the transmission component of the models in accordance with updated Planning Guide and newly created PGDTF Procedure Manual. • Each GO provides data through the resource asset registration process necessary for building and maintaining the generator component of the models in accordance with updated Planning Guide, newly created PGDTF Procedure Manual and Resource Registration Glossary. (PGRR046 - Approved 10/11/2016) ERCOT Grid Coordination Team and ROS' PGDTF responsibility
R3 | Each responsible entity, as determined in R1, shall have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1 | Yes | Yes |  |  | Medium | Long-term Planning | Requirement R3 allows a responsible entity the flexibility to determine the System steady state voltage criteria for System steady state performance in Table 1. Steady state voltage limits are an example of System steady state performance criteria. |  | ERCOT will coordinate with the TPs through the ROS' PGDTF on the development of the criteria for acceptable System steady-state voltage performance.
R4 | Each responsible entity, as determined in R1, shall complete a GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon once every 60 calendar months. This GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | Yes |  |  |  | High | Long-term Planning | The GMD Vulnerability Assessment includes steady state power flow analysis and the supporting study or studies using the models specified in Requirement R2 that account for the effects of GIC. Performance criteria are specified in Table 1. At least one System On-Peak Load and at least one System Off-Peak Load must be examined in the analysis. Distribution of GMD Vulnerability Assessment results provides a means for sharing relevant information with other entities responsible for planning reliability. Results of GIC studies may affect neighboring systems and should be taken into account by planners. The GMD Planning Guide developed by the NERC GMD Task Force provides technical information on GMD-specific considerations for planning studies. It is available at: http://www.nerc.com/comm/PC/Geomagnetic%20Disturbance%20Task%20Force%20GMDTF%202013/GMD%20Planning%20Guide_approved.pdf The provision of information in R4, Part 4.3, shall be subject to the legal and regulatory obligations for the disclosure of confidential and/or sensitive information. |  | • ERCOT in conjunction with TPs develops study scope for performing the GMD Vulnerability Assessment and documents summarized results of the steady-state analysis. Using process similar to the RTP. • ERCOT in conjunction with TPs performs a GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon for the ERCOT System. Using process similar to the RTP. • A TP may perform a GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon for its system. The TP will resolve any differences between its study and ERCOT's study with ERCOT.
4.1. | The study or studies shall include the following conditions:
4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and
4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon.
4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements in Table 1.
4.3. | The GMD Vulnerability Assessment shall be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners, and to any functional entity that submits a written request and has a reliability-related need.
4.3.1. | If a recipient of the GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments.
R5 | Each responsible entity, as determined in R1, shall provide GIC flow information to be used for the transformer thermal impact assessment specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | Yes |  |  |  | Medium | Long-term Planning | This GIC information is necessary for determining the thermal impact of GIC on transformers in the planning area and must be provided to entities responsible for performing the thermal impact assessment so that they can accurately perform the assessment. GIC information should be provided in accordance with R5 as part of the GMD Vulnerability Assessment process since, by definition, the GMD Vulnerability Assessment includes documented evaluation of susceptibility to localized equipment damage due to GMD. The maximum effective GIC value provided in Part 5.1 is used for transformer thermal impact assessment. GIC(t) provided in Part 5.2 can alternatively be used to convert the steady-state GIC flows to time-series GIC data for transformer thermal impact assessment. | This information may be needed by one or more of the methods for performing a thermal impact assessment. Additional guidance is available in the Transformer Thermal Impact Assessment white paper: http://www.nerc.com/pa/Stand/Pages/Project-2013-03-Geomagnetic-Disturbance-Mitigation.aspx A Transmission Owner or Generator Owner that desires GIC(t) may request it from the planning entity. The planning entity shall provide GIC(t) upon request once GIC has been calculated, but no later than 90 calendar days after receipt of a request from the owner and after completion of Requirement R5, Part 5.1. The provision of information in Requirement R5 shall be subject to the legal and regulatory obligations for the disclosure of confidential and/or sensitive information. | • ERCOT provides GIC flow information to be used for the transformer thermal impact assessment specified in R6 to each TO and GO. Using process similar to the RTP. • If a TP calculates GIC flows for its own system, it should work with ERCOT to resolve any differences between its GIC flows and ERCOT's GIC flows.
5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area.
5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1.
R6 | Each Transmission Owner and Generator Owner shall conduct a thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A per phase or greater. The thermal impact assessment shall: |  |  | Yes | Yes | Medium | Long-term Planning | Only those transformers that experience an effective GIC value of 75 A per phase or greater require evaluation in R6. The justification is provided in the Thermal Screening Criterion white paper. The thermal impact assessment (TIA) may be based on manufacturer-provided GIC capability curves, thermal response simulation, thermal impact screening, or other technically justified means. The transformer TIA will be repeated or reviewed using previous assessment results each time the planning entity performs a GMD Vulnerability Assessment and provides GIC information as specified in R5. | Approaches for conducting the assessment are presented in the Transformer TIA white paper posted on the project page. http://www.nerc.com/pa/Stand/Pages/Project-2013-03-Geomagnetic-Disturbance-Mitigation.aspx TIA's are provided to the planning entity, as determined in R1, so that identified issues can be included in the GMD Vulnerability Assessment (R4), and the Corrective Action Plan (R7) as necessary. TIA's of non-BES transformers are not required because those transformers do not have a wide-area effect on the reliability of the interconnected Transmission system. The provision of information in R6 Part 6.4 shall be subject to the legal and regulatory obligations for the disclosure of confidential and/or sensitive information. | TOs and GOs are responsible for the thermal impact assessment for their transformers.
6.1. | Be based on the effective GIC flow information provided in R5;
6.2. | Document assumptions used in the analysis;
6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any;
6.4. | Be performed and provided to the responsible entities, as determined in R1, within 24 calendar months of receiving GIC flow information specified in R5 Part 5.1.
R7 | Each responsible entity, as determined in R1, that concludes, through the GMD Vulnerability Assessment conducted in R4, that their System does not meet the performance requirements of Table 1 shall develop a Corrective Action Plan addressing how the performance requirements will be met. The Corrective Action Plan shall: | Yes | Yes |  | ??????? | High | Long-term Planning | Corrective Action Plans are defined in the NERC Glossary of Terms: A list of actions and an associated timetable for implementation to remedy a specific problem. Corrective Action Plans must, subject to the vulnerabilities identified in the assessments, contain strategies for protecting against the potential impact of the Benchmark GMD event, based on factors such as the age, condition, technical specifications, system configuration, or location of specific equipment. Chapter 5 of the NERC GMD Task Force GMD Planning Guide provides a list of mitigating measures that may be appropriate to address an identified performance issue. The provision of information in Requirement R7, Part 7.3, shall be subject to the legal and regulatory obligations for the disclosure of confidential and/or sensitive information. |  | ERCOT in conjunction with TPs will coordinate with the TOs' and GOs' the development of the Corrective Action Plans and review the Corrective Action Plans using a process similar to the RTP.
7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:
• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Special Protection Systems. • Use of Operating Procedures, specifying how long they will be needed as part of the Corrective Action Plan. • Use of Demand-Side Management, new technologies, or other initiatives.
7.2. | Be reviewed in subsequent GMD Vulnerability Assessments until it is determined that the System meets the performance requirements contained in Table 1
7.3. | Be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), functional entities referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need.
7.3.1. | If a recipient of the Corrective Action Plan provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments

## Applicability
4.1. |  | Functional Entities:
| 4.1.1 | Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2;
| 4.1.2 | Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2;
| 4.1.3 | Transmission Owner who owns a Facility or Facilities specified in 4.2;
| 4.1.4 | Generator Owner who owns a Facility or Facilities specified in 4.2.
4.2. |  | Facilities:
| 4.2.1 | Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage than 200 kV
Rationale:
Instrumentation transformers and station service transformers do not have significant impact on geomagnetically-induced
current (GIC) flows; therefore, these transformers are not included in the applicability for this standard.
Terminal voltage describes line-to-line voltage.

## Table 1
Table 1 –Steady State Planning Events
Steady State:
a. Voltage collapse, Cascading and uncontrolled islanding shall not occur.
b. Generation loss is acceptable as a consequence of the planning event.
c. Planned System adjustments such as Transmission configuration changes and re-dispatch of generation are allowed if such adjustments are executable within the time duration applicable to the Facility Ratings.
Category | Initial Condition | Event | Interruption of Firm Transmission Service Allowed | Load Loss Allowed
GMD | 1. System as may be postured in response to space weather information1, and then | Reactive Power compensation devices and other Transmission Facilities removed as a result of Protection System operation or Misoperation due to harmonics during the GMD event | Yes3 | Yes3
GMD Event | 2. GMD event2
with Outages
Table 1 – Steady State Performance Footnotes
1. The System condition for GMD planning may include adjustments to posture the System that are executable in response to space weather information.
2. The GMD conditions for the planning event are described in Attachment 1 (Benchmark GMD Event).
3. Load loss as a result of manual or automatic Load shedding (e.g. UVLS) and/or curtailment of Firm Transmission Service may be used to meet BES performance requirements during studied GMD conditions. The likelihood and magnitude of Load loss or curtailment of Firm Transmission Service should be minimized.