## Slide 1
UFLS Discussion
Matt Mereness
Director of Compliance
October 27, 2016

## Slide 2: UFLS Discussion outline
Background on ERCOT Compliance survey
Examples of issues and questions with handling Load Resources in survey
Differences between Annual Survey and Ops/Planning
Other emerging issues

## Slide 3: Background on UFLS Survey Requirement
ERCOT Compliance coordinates and conducts an annual survey with the TSPs and DSPs to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event as required by table below from Operating Guides 2.6.1(1) Requirements for Under-Frequency Load Shedding:
2016 results were 7.2% / 12.2% / 12.6% for total of 31.23%

## Slide 4: Current Issues with UFLS
ERCOT Compliance has been asked questions (at OWG) that may point to clarifying the assumptions for measurement of UFLS in the survey, as well as emerging operational concerns.
For reference:
NERC Requirements reflect Planning Coordinator shall have a “UFLS program design”
  See Appendix for NERC details
Operating Guide 2.6.1 is the design of ERCOT Automatic Load Shedding
  In effect since zonal Operating Guides in 2010
Issues:
For the survey just reviewed, current OpGuide language reflects the approach of “At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.”
  Survey data collected does not identify or align circuits with Load Resources for exclusion
There has also been some “double-counting” discussions over whether Load Resources that deploy at 59.7 Hz can be counted towards the UFLS response at 59.3Hz
Notes: Weather 5/12/2015 at 11:00 was mild again this year.

## Slide 5: Example
Load 20MW
Load 20MW
Load 20MW
Load 20MW
Load 20MW
LR = 1MW
Current Annual Survey language would imply this methodology:
Actual System Load = 100 MW
#1
#2
#4
#3
#5
LR = 10MW
TDSP
X
X
Survey System Load = 100 – 40 (Feeders with any LR) = 60 MW
TDSP Breaker #1 armed at 59.3 = 20MW shed (20/60 = 33%)
TDSP Breaker #2 armed at 58.9 = 20MW shed (20/60 = 33%)
TDSP Breaker #3 armed at 58.5 = 20MW shed (20/60 = 33%)

## Slide 6: Example
Load 20MW
Load 20MW
Load 20MW
Load 20MW
Load 20MW
LR = 1MW
ERCOT assumption in Planning and Operations:
System Load at 60Hz = 100 MW
#1
#2
#4
#3
#5
LR = 10MW
TDSP
X
X
System Load in EEA3 or 59.7 = 100 – 11MW LR = 89 MW
TDSP Breaker #1 armed at 59.3 = 20MW shed (20/89 = 22%)
TDSP Breaker #2 armed at 58.9 = 20MW shed (20/89 = 22%)
TDSP Breaker #3 armed at 58.5 = 20MW shed (20/89 = 22%)
Load 19MW
----------------
Load 10MW
-----------------

## Slide 7: Emerging Issues and Conclusion
Emerging issues
Because of scenario of UFLS event when in an EEA, ERCOT does not believe double-counting of Load Resources should be allowed for UFLS 5/10/10 performance.
Similar to Load Resources, load amounts that are shed from ERS should also not contribute to UFLS performance.
Distributed Energy Resources are not considered in language at this point.
Conclusion and possible issues to consider resolution to:
Inconsistency in UFLS Survey and Ops/Planning
  Address exemption of entire circuits equipped with Load Resources in survey
Potentially out-of-date language in Protocols and Guides may be worth re-alignment
  Consistent handling of Load Resource and ERS
  Any considerations for DERs

## Slide 8: Appendix
NERC standard PRC-006-2 — Automatic Underfrequency Load Shedding:
Requirement 9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. [VRF: High][Time Horizon: Long-term Planning]
Measurement 9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9.