## Slide 1
Metering Working Group Update
Darrell Sumbera – CenterPoint Energy
Metering Working Group Chair
WMS Meeting, November 2, 2016
November 2, 2016

## Slide 2: SMOGRR 018
Synopsis:
  This Settlement Metering Operating Guide Revision Request (SMOGRR) allows an ERCOT-Polled Settlement (EPS) Meter to be installed for a facility that is connected to a three-wire wye, high or low impedance grounded distribution system, if the high or low impedance ground is installed as part of a fault monitoring system for the facility and no phase to ground loads or phase to ground sources are connected behind the metering point.
<number>
Notes: <number>

## Slide 3: SMOGRR 018
Review:
  On 9/22/16, the Meter Working Group (MWG) was in consensus to recommend approval of SMOGRR018 as submitted.
  On 10/20/16, MWG was in consensus to endorse and forward to WMS the 9/22/16 MWG Report and Impact Analysis for SMOGRR018.
Requested action from WMS:
  Recommend approval of SMOGRR018 as submitted
<number>
Notes: <number>

## Slide 4: SMOGRR 019
Synopsis:
  SMOGRR 019
    Provides updates and clarifications for determining the connected burden on current transformers when used in a parallel configuration;
    Requires TDSP’s to provide nameplate photos of newly installed instrument transformers; and
    Provides increased clarity and consistency for the market on loss of potential alarms programed into EPS Meters.
<number>
Notes: <number>

## Slide 5: SMOGRR 019
Review:
  On 9/22/16, the Meter Working Group (MWG) was in consensus to recommend approval of SMOGRR019 as revised by MWG.
  On 10/20/16, MWG was in consensus to endorse and forward to WMS the 9/22/16 MWG Report and Impact Analysis for SMOGRR019.
Requested action from WMS:
  Recommend approval of SMOGRR019 as recommended by the MWG in the 10/20/16 MWG Report, with a recommendation that revisions to paragraph (k) of section 6.5.4(1) be implemented 1/1/2018, and for all other revisions to be implemented upon TAC approval
<number>
Notes: <number>