## Slide 1
Phase Angle Limitations
Stephen Solis
System Operations Improvement Manager
November 3, 2016

## Slide 2: Overview
NERC Standards Glossary of Terms
  Operational Planning Analysis
  Real Time Assessments
Why monitor phase angle limitations?
NPRR 790
Phase Angle Limitations
  Limit Exceedances
  Operational Measures
Next Steps

## Slide 3: NERC Glossary of Terms
Operational Planning Analysis (OPA) - An evaluation of projected system conditions to assess anticipated (pre-Contingency) and potential (post-Contingency) conditions for next-day operations. The evaluation shall reflect applicable inputs including, but not limited to, load forecasts; generation output levels; Interchange; known Protection System and Special Protection System status or degradation; Transmission outages; generator outages; Facility Ratings; and identified phase angle and equipment limitations. (Operational Planning Analysis may be provided through internal systems or through third-party services.)
Real Time Assessment (RTA) - An evaluation of system conditions using Real-time data to assess existing (pre-Contingency) and potential (post- Contingency) operating conditions. The assessment shall reflect applicable inputs including, but not limited to: load, generation output levels, known Protection System and Special Protection System status or degradation, Transmission outages, generator outages, Interchange, Facility Ratings, and identified phase angle and equipment limitations. (Real-time Assessment may be provided through internal systems or through third-party services.)

## Slide 4: NERC Glossary of Terms
New Definitions become mandatory and effective on January 1, 2017.
Between January 1, 2017 and April 1, 2017, requirement only applies to OPA and RTA for IROL. [IRO-008-1, IRO-009-2]
Beginning April 1, 2017 requirement will apply to all SOLs including the IROL. [IRO-008-2, IRO-009-2, TOP-001-3]
ERCOT is responsible for Reliability Coordinator requirements to conduct OPAs and RTAs, including the evaluation for phase angle limitation exceedances.
It is anticipated that the Transmission Operator Coordination Functional Registration (CFR) agreement will assign responsibility to ERCOT for conducting OPAs and RTAs for Transmission Operator requirements, including the evaluation for phase angle limitation exceedances.

## Slide 5: Why monitor phase angle limitations?
Phase angle limitation was a contributing cause to the September 8, 2011 Southwest event.
  Recommendation #27: TOPs should have: (1) the tools necessary to determine phase angle differences following the loss of lines; and (2) mitigation and operating plans for reclosing lines with large phase angle differences. …
NERC Project 2014-03 Standard Drafting team addressed this concern by including the phase angle limitations in the previously shown definitions.

## Slide 6: Why monitor phase angle limitations?
When a transmission line trips or goes out of service, the phase angle will generally increase between its two terminal points.
If the phase angle is too large, closing the line breaker back into service with a large angle difference may result in damage to nearby generator turbine shafts, and the resulting power swings and oscillations could lead to system instability or collapse.
Phase angle limitations have been implemented by ERCOT TSPs on some synchronism-check relays to prevent some of the negative effects of closing a line breaker back into service with a large phase angle difference.
By monitoring phase angles vs the phase angle limitations pre-contingency and post contingency, situational awareness is enhanced to plan for and take coordinated actions to allow for lines to be safely closed back in.

## Slide 7: NPRR 790
A one-time survey was conducted in spring of 2016 to identify all known phase angle limitations.
These limitations were identified as part of NPRR 790 to be synchronism check relay phase angle limitation applied to operator initiated, non-automated control actions on Transmission breakers.
These limits are being uploaded into the Network Operations Model and ERCOT Energy Management System (EMS) to allow ERCOT to evaluate for phase angle limitation exceedances as part of its OPA and RTA.
NPRR 790 is meant to provide a mechanism for maintaining phase angle limitation data points in the Network Operations Model by the TSPs through the existing Network Operations Model Change Request (NOMCR) process.
This information is necessary for ERCOT to conduct its OPA and RTA consistent with IRO-010-2 and TOP-003-3 NERC Reliability Standards which become mandatory and effective on January 1, 2017.

## Slide 8: Phase Angle Limitations
ERCOT’s survey assessed 345kV, 138 kV, and 69kV.
ERCOT received a variety of phase angle limitations between 10 degrees to 60 degrees.
Some TSPs utilized consistent settings or approach company wide while others had more variations.
Some TSPs do not utilize or arm synchronism check relays.
IEEE PC37.104 GUIDE FOR AUTOMATIC RECLOSING OF CIRCUIT BREAKERS for AC DISTRIBUTION AND TRANSMISSION LINES was referred to as a guide by one TSP.

## Slide 9: Phase Angle Limitation Exceedances
ERCOT will begin monitoring for phase angle limitation exceedances in early December of 2016.
This monitoring will occur in Outage Coordination studies, Next Day studies (OPA), and Real Time studies (RTA).
Corrective actions for phase angle limitation exceedances may include but are not limited to:
  Creating, or implementing a Constraint Management Plan (e.g. TOAP) to allow for coordinated actions to either allow for line to remain open or for angle difference to be reduced
  Creating a manual constraint (e.g. Generic Transmission Constraint) resulting in appropriate re-dispatch
  Commitment of generation to allow for redispatch
  Recalling transmission outages

## Slide 10: Phase Angle Limitation Exceedances
If a phase angle limitation exceedance is observed in the Outage Coordination or Next Day studies (OPA) time frame, a Constraint Management Plan (CMP) may be created to resolve the post contingency exceedance or other alternative actions will be taken as necessary.
If a post-contingency phase angle limitation exceedance is observed in the Real Time studies time frame (RTA), a CMP may be created to resolve the post contingency exceedance or other alternative actions will be taken as necessary.
If a pre-contingency exceedance phase angle limitation exists in RTA, a CMP will be implemented or other alternative actions will be taken as necessary.
ERCOT is anticipating the potential need for providing feedback to TSPs on reevaluating their phase angle limitations if the limitations are exceeded frequently.

## Slide 11: Resolving Phase-Angle Exceedances
Objective for any corrective actions will be to reduce the phase angle difference to within the limitation to allow for the line to be closed back in service.
The line may be planned to remain open for a longer duration if studies can demonstrate that with the line open, the ERCOT system will remain secure for any subsequent N-1 contingencies.
ERCOT and ERCOT TOs should coordinate to consider timeliness of any corrective actions.
Priority should be given to 345kV and 138kV lines respectively.

## Slide 12: Next Steps
ERCOT will begin monitoring the phase angle limit exceedances beginning early December 2016.
ERCOT will begin taking action on the phase angle limit exceedances on January 1, 2017.
ERCOT will send a Market Notice reminding Market Participants of the January 1, 2017 change.
NPRR 790 will be implemented on January 1, 2017 barring any issues.

## Slide 13: Questions?