## Slide 1
Far West Texas Transmission Project -
ERCOT Independent Review
November 15, 2016

## Slide 2: Overview
AEPSC and Oncor jointly submitted Far West Texas Project (FWTP) for Regional Planning Group review. This is a Tier 1 project that is estimated to cost $ 423 million.
  Proposed for 2021 to 2022 timeframe
  Addresses petroleum related load forecasts
  Reliability Issues
    Voltage Collapse
    Loss of Load
    Short-Circuit Strength & System Protection
  Provide Operational Flexibility
  Provides future upgrade path for Far West Region

## Slide 3: Study Assumptions
Steady-State Study Case
  Constructed from latest 16RTP reliability case 16RTP_2021_SUM_WFW
  Study Region will consist of Far-West and West Weather Zones
  Generator additions that meet Planning Guide Section 6.9 criteria in study region at time of study will be added to the case.
  The study case will employ the same adjustments as the 2016 RTP case unless stated otherwise herein.
  Transmission Projects expected to be in-service within the study region by 2021 at the time of the study will be added to the case
  Apply 2021 petroleum related load forecasts
    Culberson loop: 426 MW
    Barilla Junction Area lines: ~ 511 MW
  N-1 SCOPF Dispatch

## Slide 4: Contingencies and Criteria
Initial Steady-State Reliability Analysis
  Contingencies for Study Region
    NERC TPL-001-4 and ERCOT Planning Criteria (http://www.ercot.com/content/wcm/current_guides/53526/04_050115.doc ):
      P0
      P1-1, P1-2, P1-3, P1-4,
      P2-1, P2-2, P2-3 (All EHV only)
      P3-1, P3-2, P3-3, P3-4, G-1+P7 {G-1 worst case only}
      P4-1, P4-2, P4-3, P4-4, P4-5 (All EHV only)
      P5-1, P5-2, P5-3, P5-4, P5-5 (All EHV only)
      P6-2: X-1 + (P1-1, P1-2, P1-3, P1-4, P7-1) {X-1 is 345 kV Auto outages}
      P7-1
  Criteria:
    Thermal
      Monitor all transmission lines and transformers in study region (excluding GSU)
      Use Rate A for Normal Conditions
      Use Rate B for Emergency Conditions
    Voltages
      Monitor all busses 100 kV and above
      0.95 < 1.05 Normal
      0.90 < 1.05 Emergency
      Voltage deviations exceeding 8% on non-radial load busses

## Slide 5: Study Procedure
Scenarios to be evaluated:
  Study Case
  Higher Culberson Loop Load
    Same as study case but with Higher Load on Culberson Loop
    Represents “Potential” Culberson Loop load submitted to ERCOT by Oncor
  Zero Solar Scenario
    Same as study case but with 0 MW Solar dispatched in study region
  Sensitivities based on PGRR0042:
    Generator additions with Signed Interconnection Agreements but that DO NOT meet Planning Guide Section 6.9 criteria in study region at time of study will be added to the case

## Slide 6: Dynamic Reliability Analysis
Dynamic Stability Study Case
  Constructed from latest DWG 2021SUMPEAK Flat Start case
  Be consistent with steady state analysis assumptions
  Criteria: NERC TPL and ERCOT Planning Guides

## Slide 7: Deliverables
  Tentative Timeline
    January 2017 – Findings
    February 2017 – Final Report

## Slide 8
?
Stakeholder Comments Also Welcomed Through:
rpg@ercot.com