## Slide 1
Probabilistic Transmission Planning - ERCOT
(November 16, PLWG)

## Slide 2: Contents
Introduction
Deterministic Vs Probabilistic
Applications
Efforts and Issues
Next Steps & Summary
Appendices

## Slide 3: Introduction
Motivation
  Increasing uncertainties (intermittent generation, distribution, weather pattern) are expected in ERCOT system
  NERC reliability standard requires to test a large number of contingencies and identify contingencies with severe impact
ERCOT and others within the industry are currently researching probabilistic transmission planning methods and tools. It is believed that deterministic planning processes can be enhanced by supplementing with a probabilistic planning approach
The probabilistic planning concept is not new but not popular mainly because of the deterministic nature of planning standards, lack of tools, and lack of data

## Slide 4: Deterministic vs Probabilistic Transmission Planning
Deterministic Approach
Reliability Analysis is done assuming each contingency is certain
System issues (thermal loading, voltage, etc.)
Several cases for certain operating conditions (e.g. summer peak and off peak) based on engineering judgement
Probabilistic Approach
Risk Assessment (Risk = Impact x probability of events and scenario)
(e.g. Expected Unserved Energy)
Reliability Analysis is done for each contingency that has outage statistics (frequency and duration).
System issues (thermal, voltage, etc.) as well as Impact (e.g. load curtailment)
A large number of cases covering a wide spectrum of operating conditions by considering uncertainties of weather, intermittent generation, load forecast, economic, distribution side.
Probability is assigned to each case
Drawbacks of Deterministic Approach
does not cover various system conditions nor consider many uncertainties in a system
ignores likelihood of system conditions and the probability of events

## Slide 5: Example: Magnitude of Risk Associated with Critical Event

## Slide 6: Applications
Development of a number of credible study cases with many uncertainties considered
Identification of critical planning or extreme events using likelihood, system impact or magnitude of risk associated with each event
Evaluation of project alternatives in terms of benefit (e.g. test deeper contingencies such as substation outage: compute expected unserved energy (EUE) or incremental reliability index (IRI) to compare reliability benefit of each option
Identification of weak areas based on the number of interruption of load at each bus, number of occurrence of thermal or voltage issues on line or bus
Measure the health of real-time system (e.g. by computing EUE periodically)

## Slide 7: ERCOT’s Efforts
Mid 2014~1st qtr. 2015
ERCOT started to participate in the EPRI Risk-based Transmission Planning Program
Goal: Develop basic concept, risk-based analysis method, metrics, data requirement guideline, new tools and improving existing tool for probabilistic planning
1st qtr. 2015~1st qtr. 2016
EPRI performed a case study using the data ERCOT provided:
1st qtr. 2016~present
ERCOT’s Review on EPRI’s Case Study and Tools
Using the cases and input data, ERCOT performed the analysis using the tools
Deliverables: 1) Technical document of the RBTP, 2) Prototype of tools (e.g. TransCARE, Outage statistic creation, Risk-based Scenario Builder)
EPRI’s ERCOT Case Study
11 years of weather, historical wind and load data, and economic load forecast error to create a number of system conditions
Transmission network models, contingency definitions
Outage statistics from NERC TADS and GADS
Deliverables: 1) Technical document of the case study, 2) Improved version of the tools (TransCARE, Risk-based Scenario Builder), 3) Cases and input data used for ERCOT Case study
Delivered the issues to EPRI so the tools can be fixed and improved
Identified many issues in tools and areas to improve, documented the problems and created user-guide
For the proof of concept, ERCOT tested three transmission options using cases representing various system condition and extreme events such as substation outages and common right or way. The result has been delivered
Value: 1) Increase system reliability by considering deeper contingencies, 2) Incorporate some of the uncertainties, 3) Help us make a better decision on transmission investment

## Slide 8: Framework of Probabilistic Risk Assessment
Case Development
Tool: EPRI’s Risk-based Scenario Builder
Output: cases in PTI format, probability of each case, deeper contingencies (optional)
Reliability Analysis
Tool: EPRI’s TransCARE or PSS/E, Outage Statistics Creation Tool
Risk Assessment
Tool: EPRI TransCARE or PSS/E
Input: system impact (MW curtailment) associated with each contingency, probability of each critical contingency
Key issues to be resolved:
How many cases need to be drawn to minimize the chances of missing critical operating conditions? Are those cases valid?
Input: historical data (11 year weather, renewable, load), 5 different load forecast errors, network model (RTP case), outage statistics (optional)
Output: criteria violations, system impact (e.g. load curtailment), outage statistics of each event
Key issues to be resolved:
Sensitive to slight change in operating condition resulting in Inconsistent result of system impact, numerous non-converged contingencies and tools not capable of calculating load curtailment for voltage collapse
Output: risk metrics
(e.g. EUE or IRI)
Input: cases, contingencies, user-defined contingencies, outage statistics of each element (e.g. NERC TADS or GADS data)
Key issues to be resolved:
Data is the key to this probabilistic analysis. Outage statistics are needed for various contingency types (P1~P7) and extreme event

## Slide 9: TransCARE (Transmission Contingency And Reliability Evaluation)
TransCARE, an improved version of an older EPRI program known as Transmission Reliability Evaluation for Large-Scale System (TRELSS), is designed for probabilistic reliability analysis
Power Flow Cases
Input data including outage statistics
Probabilistic Reliability Assessment
(TransCARE)
Reliability Indices

## Slide 10: TransCARE (cont.)
Input files to TransCARE:
  Power flow case: *.sav in PSSE version 32, or GE PSLF. Up to 10 cases
  Contingency: up to N-9 can be handled. Up to 1 million contingencies
  Outage Statistics: outage frequency and duration of each element
  Other optional files: Common mode outage data, breaker location data, generation dispatch data and load data
Reliability Analysis and Remedial Actions:
  Available solution methods: DC and AC Full NR
  Reliability analysis: Circuit loading, high/low bus voltage, voltage deviation, etc.
  Remedial actions: Load curtailment, generation/shunt/transformer adjustments
  Protection Control Group (PCG) Analysis: simultaneously trip elements when a fault occurs anywhere within their primary protection zone.
Reliability indices calculated:
  Frequency, Duration, and Severity of system problems (by bus, circuit, and for study area)
  Frequency, Duration and Severity of load curtailment as well as unserved energy (by bus and for study area as well as by contingency)

## Slide 11: Key Issues To Be Resolved
  Tools are research-grade. Significant improvement needed for tools
  Tools should be capable of computing system impact (e.g. MW load curtailment) to eliminate non-convergence (e.g. voltage collapse) in terms of MW load curtailment
  Results (e.g. MW load curtailment) need to be verified. TransCARE is very sensitive even for a slight change in a system
  Cases developed from RBSB tool needs to be verified. The number of cases to draw and study should be researched and determined
  Even if cases and tools are perfect, it may take longer time depending on the scope of study (e.g. a number of study cases, number of contingency combinations)

## Slide 12: Key Issues To Be Resolved (cont.)
Availability of outage statistics
  Probabilistic data requires outage data of transmission elements and generators
  Nation-wide generic data: NERC GADS (generator outage data for decades), TADS (transmission with 200 kV above since 2008), Canadian Electricity Association (CEA, greater than 60 kV since 1980)
  Best practice is using ERCOT region-specific data (by weather zone, by event type (P1~P7, EE), by voltage level). These are currently not available
Criteria is not available (e.g. threshold associated with system impact, probability of event, magnitude of risk) that triggers action

## Slide 13: Next Steps
Tentative Schedule | Description
Present ~ 2018 | Continue to engage in EPRI’s R&D project Collect historical outage data for ERCOT system (e.g. voltage level, automatic vs non-automatic, cause, fault type, time/load level, weather zones), and investigate statistics such as P4, P5, P7, EE2 Analyze outage data collected and review against other statistics (e.g. NERC TADS, GADS or EPRI data) Attempt to address the challenges identified and continue to work with EPRI to address issues with tools and more (e.g. cases, tools, statistics, criteria, metrics) Test potential applications (ranking contingencies, risk metrics)
Beyond 2018 | Continue to work with others in industry on the success of this concept Continue to work on gathering historical outage data Engage in EPRI program if exists Consider risk metric(s) in decision-making (e.g. Evaluation of multiple options in ERCOT independent review)

## Slide 14: Summary
Probabilistic transmission planning approach is great idea and can be supplemental to the traditional deterministic planning process
A number of issues with tools, data and criteria need to be addressed
ERCOT will continue to work with others in industry and research institutes
  To investigate probabilistic transmission planning approach
  To address challenges and ultimately to apply this approach to the current planning process

## Slide 15: Appendix: Example - Probability of occurrence for load and wind output based on historical data

## Slide 16: Appendix: Expected Unserved Energy or Incremental Reliability Index
Incremental Reliability Index (IRI) = reliability improvement per million dollar
Expected Unserved Energy (EUE)
EUE before project - EUE after project
Capital cost of project ($M)
* Note: EUE can be calculated for all cases tested and probability of each case need to be multiplied)

## Slide 17: Appendix: Issues and Suggested Improvements
EPRI Scenario Creation Tool (RBPSB)
1. Generators dispatch to include reserve not losses
2.Does not randomly sample scenarios
3.Does not have enough information to map output back to input data
4.Does not solve and validate re-dispatched power flow scenarios
5.Output does not include probability of scenarios and strata
6. Unclear documentation on sampling scenarios based on distribution within strata
TransCARE
1. Questionable remedial actions
2. Post contingency power flow solving issues(diverge, large mismatch)
3. Does not recognize unrealistic contingencies (a filter function is needed)
4. Does not keep a track of skipped must-run contingencies
5. Enumeration does not work properly
6. Report data format needs to be improved
7. Better documentation on EUE calculation methodology is needed
RBPSB >> TransCARE
1.Several adjustments (defining new zones, change of swing bus, etc.) on re-dispatched power flow scenarios need to be made to be able to run in TransCARE (Manual Process)
2. TransCARE ‘s capability of handling up to 10 scenarios once might not be sufficient to implement the idea of stratified sampling. API tools are needed such that TransCARE can be run as an engine in scripts

## Slide 18
Supervisor, Transmission Planning
Principal, Grid Integration
Supervisor, Engineer Development Program
Engineer, Transmission Planning
Engineer, Resource Adequacy
Lead Engineer, Resource Adequacy
ERCOT Probabilistic Planning Team