## Slide 1
2017 Long-Term Load Forecast
Calvin Opheim
Load Forecasting & Analysis
SAWG
November 18, 2016 (revised)

## Slide 2: Outline of Today’s Presentation
Forecasting Framework / Model Data Input
Growth Driver
Normal Weather (P50) Forecast
Impact of 4 CP on Summer Peak
Assumptions and Challenges

## Slide 3: Outline of Today’s Presentation
Active Models
ERCOT P50 Forecast
Weather Zone P50 and P90 Forecasts
Questions

## Slide 4
Forecasting
Framework

## Slide 5: Weather Zones
Two or three weather stations located in each weather zone
Notes: WEST peak was in July

## Slide 6: Load Forecasting Models
Hourly Models
  Hourly models were created for each weather zone
  Over 48,000 hourly observations including load, weather data, and calendar variables (day-of-week, holidays, etc.)
  Historical data from January 2011 through August 2016 was used to create the models
  Unique model for each season
Rationale
  Typically use 5 years of historical data in model development
  Allows for a more recent snapshot of appliance stock, energy efficiency impacts, demand response impacts, price responsive load, etc.

## Slide 7: Load Forecasting Models – Data Input
Weather Data
  Temperature, Temperature Squared, Temperature Cubed
  Cooling Degree Days
  Heating Degree Days
  Cloud Cover
  Wind Speed
  Dew Point
  May also include values from a previous hour(s) or day(s)

## Slide 8: Load Forecasting Models – Data Input
Calendar
  Month
  Day of the week
  Holidays
  Hour
  Interact Hour with Day of the week

## Slide 9: Load Forecasting Models – Data Input
Variable Interactions
  Interact weather variables with calendar variables
  Examples: Temperature with Hour, Dew Point with Hour
  Interact multiple weather variables with calendar variables
  Example: Temperature with Dew Point and Hour

## Slide 10
Growth Driver

## Slide 11: Load Forecasting Models – Data Input
Monthly Premise Count by Customer Class
  Instead of using economic measures as the driver of future load growth, use the actual number of premises for each customer class
  Customer class is determined by the load profile assignment
  Three classes
    Residential (includes lighting)
    Commercial
    Industrial
Notes: Mention history of changing from using purely economic forecast. Historical economic values are subject to change two years after the fact.

## Slide 12: Forecasting Premises
Premise Models
  Forecasted premise counts are used as the driver of future demand/energy growth in the majority of weather zones
  Economic variables were used as input in the premise forecast models
  Variables used include population, non-farm employment, and housing stock
  Also included error correction term

## Slide 13: Forecasting Premises
Monthly Economic Measures
  Non-farm employment
  Population
  Housing stock
  Moody’s base scenario was used for economic forecasts
Data Availability
  County level
  Counties are mapped into a weather zone
Growth Driver in Premise Models

## Slide 14: Forecasting Premises - Challenges
Premise counts were increased significantly via opt-in
Forecasting premises is problematic

## Slide 15: Forecasting Premises - Challenges
Premise counts were increased significantly via opt-in
Forecasting premises is problematic

## Slide 16: Forecasting Premises - Challenges
Non-farm employment and housing stock have a negative correlation with premises
Forecasting premises is problematic

## Slide 17: Load Forecasting Models – Data Input
Monthly Economic Data
  For the three weather zones without a premise forecast (Far West, West, and North), use economic data (population or non-farm employment) as the driver of future load growth
Moody’s Base Scenario

## Slide 18: Forecasting Premises
Premise Models - Exceptions
  Unable to forecast premise counts in three weather zones
  Impacted by an entity opting-in (Far West and West)
  Premises declining (North)
Modeling Solution
  These three weather zones required traditional economic variables (population and non-farm employment) as the driver of future demand/energy growth in the hourly models

## Slide 19
Normal Weather
(P50) Forecast
Notes: Comment on not directly temperature based

## Slide 20: Normal Weather (P50) Forecast
Performed at the Weather Zone Level
  Historical weather from calendar years 2002 – 2015 is used as input into each hourly weather zone forecast model

## Slide 21: Normal Weather (P50) Forecast
Performed at the Weather Zone Level
  Forecasted values are sorted from high to low for using each historical weather year as input
  The sorted values are averaged by rank
  Example:
  Below are the top 5 peak values for Coast for 2017 using 2002 – 2015 historical weather data

## Slide 22: Normal Weather (P50) Forecast
Performed at the Weather Zone Level

## Slide 23: Normal Weather (P50) Forecast
Performed at the Weather Zone Level
  This process is completed for every weather zone, for each forecasted year (2017 – 2026)
P50 forecasts for each weather zone are found in the Weather Zone Forecasts section of this presentation

## Slide 24: Normal Weather (P50) Forecast
ERCOT (P50) Forecast
  After the weather zone (P50) hourly load forecasts are completed, the results are mapped into a representative historical calendar by rank
  The 2003 calendar was selected (as has been our convention in the past). Using the 2003 calendar results in the highest peak forecast.

## Slide 25: Weather Zone Peak vs ERCOT System Peak

## Slide 26
4 CP Impacts on Summer Peak

## Slide 27: Estimate of 4 CP Impacts
Data source is the load for transmission premises from settlements (LTRANSTL)
  Using this aggregated load, determine the highest MW for each 15-minute time period during each calendar month
  Also determine the second and third highest MW for each 15-minute time period during each calendar month
  Subtract the load from the summer peak day (8/11/2016) from the highest MW value for each interval
  Subtract the load from the summer peak day (8/11/2016) from the second highest MW value for each interval
  Subtract the load from the summer peak day (8/11/2016) from the third highest MW value for each interval
  These differences approximate the 4 CP impact

## Slide 28: Estimate of 4 CP Impacts
Performed at the Weather Zone Level

## Slide 29: Estimate of 4 CP Impacts
Performed at the Weather Zone Level

## Slide 30: Estimate of 4 CP Impacts
Performed at the Weather Zone Level

## Slide 31: Estimate of 4 CP Impacts
Performed at the Weather Zone Level

## Slide 32: Estimate of 4 CP Impacts
Performed at the Weather Zone Level

## Slide 33: Estimate of 4 CP Impacts
This estimate is conservative
  Does not include impacts from the NOIEs
  Does not include the impacts from other non-transmission (distribution) premises
  Both of the above have significant weather sensitive loads which makes the estimate of 4 CP more difficult
  Requires a different technique(s) to quantify their 4 CP impact

## Slide 34
Assumptions and Challenges

## Slide 35: Load Forecasting Assumptions
Current Modeling Framework Assumes:
  Inherent levels from the input data for
    Appliance stock / energy efficiency
    Demand Response, 4 CP Impact, behind-the-meter DG, Price Responsive Load
    Electric Vehicles
  No increase in territory to be served by ERCOT
    Lubbock is not included
  No discrete increase for additional larger industrial facilities (except for Freeport)
No incremental adjustments (positive or negative) to the load forecast have been applied for the above

## Slide 36: Load Forecasting Challenges
Weather Volatility:
  Extreme weather events (record heat and cold, drought, flood, etc.) seem to occur fairly frequently
Economic Uncertainty
  Accuracy of economic forecasts
  Recession has occurred every decade since the 60s
Policy Impacts
  Behind the meter DG growth
  Energy efficiency growth
  Increased price caps
  Loads in SCED

## Slide 37
Active Models

## Slide 38: Models
ERCOT maintains an ensemble of load forecast models
  Neural Network models based on a single linear node
  Linear Regression model representation of the single linear node Neural Network model
    Uses the exact same variables, relationships as the single linear node Neural Network model
    Is easier to share the model form with Market Participants (i.e., the variables are easier to interpret than those from the Neural Network model)
    Results are very close to the Neural Network model
  Neural Network models based on linear and higher order nodes
  Models are maintained for daily energy forecasting, hourly energy forecasting, and a combination

## Slide 39
ERCOT P50 Forecast

## Slide 40: ERCOT Summer Peak Forecast
Notes: Model error is looking back.

## Slide 41: ERCOT Summer Peak Forecast
Forecast is 2% – 4% higher than the 2016 long-term load forecast
The majority of the increase is in the South Central forecast
The West and Far West forecast’s are lower than the 2016 long-term load forecast
Notes: Model error is looking back.

## Slide 42: ERCOT Annual Energy Forecast
Forecast is 0% – 3% higher than the 2016 long-term load forecast
Notes: Model error is looking back.

## Slide 43: Forecast Adjustments
Freeport LNG Facility
  Incremental load of 655 MW was added to the forecast
  Timeline for the load addition was from Freeport’s website
  (http://www.freeportlng.com/Project_Status.asp)
  This load was
  included in the
  previous forecast
  No reduction in the
  facility load was
  assumed for 4 CP
  and/or high price
  intervals

## Slide 44: ERCOT Summer Peak Demand

## Slide 45: ERCOT Annual Energy

## Slide 46
Weather Zone Forecasts

## Slide 47: 90th Percentile (P90) Forecast
Performed at the Weather Zone Level
  Forecasted values are sorted from high to low for using each historical weather year as input
  The 90th percentile is calculated for the sorted values
  Example:
  Below are the top 5 peak values for Coast for 2017 using 2002 – 2015 historical weather data

## Slide 48: Coast

## Slide 49: East

## Slide 50: Far West

## Slide 51: North

## Slide 52: North Central

## Slide 53: South

## Slide 54: South Central

## Slide 55: West

## Slide 56: Questions?