## 1) General Information
CenterPoint Energy Distribution Loss Factor for 2017 Rev 2
----> | Changes for 2017 are shown in bold red font
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses, which was updated on September 1, 2016. See following
protocol link: http://www.ercot.com/mktrules/nprotocols/current
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load (15 minute basis)
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
----> | AAL value for use in 2017 = 9,898 MWH
AAL value for use in 2016 = 9,940 MWH
AAL value for use in 2015 = 9,741 MWH
AAL value for use in 2014 = 9,290 MWH
AAL value for use in 2013 = 9,304 MWH
AAL value for use in 2012 = 9,463 MWH
AAL value for use in 2011 = 9,034 MWH
AAL value for use in 2010 = 8,785 MWH
AAL value for use in 2009 = 9,043 MWH
AAL value for use in 2008 = 8,794 MWH
Customer Coding for CenterPoint Energy:
Distribution customers that take service at secondary voltage are coded "D"
Distribution customers that take service at primary voltage are coded "E"
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
For "D" Secondary Customers
F1 = 0.016840
F2 = 0.000960
F3 = 0.020250
AAL for ERCOT (15 mins) = 9,898
For "E" Primary Customers
F1 = 0.011570
F2 = 0.000065
F3 = 0.001100
AAL for ERCOT (15 mins) = 9,898
Assumptions
1. Assume AAL for CNP corresponds to AAL for ERCOT
2. However, the peak for CNP is proportionately greater than the peak for ERCOT relative to AAL.
Ratio of Peak to AAL
|  | CNP | ERCOT
|  | 2.0302 | 1.8036
Ratio of Peak to AAL for CNP is not proportional to ERCOT
| 2014 for use in 2015 |  | 2015 for use in 2016 |  | 2016 for use in 2017
| 15 mins | 1 hour | 15 mins | 1 hour | 15 mins | 1 hour
CNP Peak | 3678.75 | 14715 | 3923.5 | 15694 | 3865 | 15460
CNP AAL | 1882.25 | 7529 | 1917.5 | 7670 | 1903.75 | 7615
ERCOT Peak | 16712.75 | 66851 | 17414 | 69656 | 17852.25 | 71409
ERCOT AAL | 9741 | 38964 | 9940 | 39760 | 9898 | 39592
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % losses (and DLF) above AAL are
increased an amount that is consistent with this higher loading at peak, so that when ERCOT hits peak, % losses will correspond to CNP peak.
Methodology upon which the calculation of loss factor was made:
Over the years, CenterPoint Energy has developed system loss equations for each part of the system. Equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. See Tab 3 - Loss Equations.
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated in 2016 for use in 2017 as follows:
1. Substation Transformer Losses (The A B constants for substation transformers were updated for 2017)
The current substation transformer database was used to determine the total "No-load" losses for all transformers on the system.
This database contains test data for every substation transformer.
The total no-load losses are 20.635 MW.
Also, the database provided the total "Load" losses for the transformers on the system at rated trf load.
This value is 58.284 MW at 17,965 MW load level.
This results in a total of 78.919 MW of substation transformer losses at approximately 17,965 MW at CNP (Sub Trf nameplate rating)
The constants in the system loss equations were adjusted to match this result. See Tab 3.
2. Primary Conductor Losses (No change in the A B constants for primary conductor for 2017)
The primary conductor losses for 2007 were considered to be similar to the losses in 2006, but the constant for the system loss
equation was increased 2.5% due to the increased loading on our circuits which is a result of our revised design criteria.
The design criteria allows higher loadings due to an increase in switching operations under contingency conditions from
2 pairs of switching operations to 4 pairs of switching operations.
For 2017, there is no further change in the system loss equations.
3. Distribution Transformer Losses (The A B constants for distribution transformers were updated for 2017)
An inventory of the distribution transformers was downloaded from the GIS system. For every size transformer
the "No-load" losses and "Load" losses were determined by various test reports. This information was entered
for each size of transformer to determine the total "No-load" losses and the total "Load" losses for the distribution transformers.
Additionally, a TLM (Transformer Load Maintenance) Program was used to calculate no-load and load losses.
Since the no-load losses used in the TLM program were based on older/higher values from 1985 and the GIS spreadsheet
used more current test values from 2000-2005, the results of the two programs were averaged together to get
a balanced result for "no-load" losses for a distribution system that has both old and new transformers.
The "load losses" from both methods were very close, so the load losses from GIS were used.
See Tab 3 for the updated A B constants for distribution transformers.
4. Secondary Conductor Losses (No change in the A B constants for secondary conductor for 2017)
The constant in the system loss equation for secondary losses for 2017 is same as used in previous years.
5. AAL for ERCOT
The AAL for ERCOT was updated based on information from ERCOT. The new value for 2017 is 9,898 MWH for 15 minutes.
DLF Coefficients (F1, F2 and F3)
For both primary and secondary customers, the F1, F2 and F3 coefficients were selected to provide a curve fit with the loss equations that were
developed above. F1 impacts the right side of the curve, F2 impacts the middle/entire curve, and F3 impacts the left side of the curve. These
coefficents were adjusted to get a curve fit in the most critical areas. See spreadsheet and graphs in Tab 2 - Loss Analysis.
The F1, F2, and F3 coefficients for D secondary customers and E primary metered customers for 2017 are shown above.
Overall results:
For "E" Primary Customers |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 for use in 2017
|  | DLF at AAL | 1.311% | 1.291% | 1.241% | 1.272% | 1.299% | 1.274%
|  | DLF at ERCOT Peak | 2.131% | 2.072% | 2.105% | 2.05% | 2.159% | 2.154%
For "D" Secondary Customers |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 for use in 2017
|  | DLF at AAL | 3.663% | 3.705% | 3.704% | 3.739% | 3.776% | 3.805%
|  | DLF at ERCOT Peak | 4.218% | 4.178% | 4.197% | 4.144% | 4.247% | 4.256%
Questions:
If you have any questions, please call Richard Moffatt at CenterPoint Energy at 713-945-4162 or Ben Kirchhofer at CenterPoint Energy at 713-207-6313
or email at richard.moffatt@centerpointenergy.com or bennett.kirchhofer@centerpointenergy.com
CenterPoint Energy Distribution Loss Factor For 2017 Rev 1
Oct 19, 2016

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 2) Loss Analysis
|  | CenterPoint Energy Distribution Loss Factor for 2017 Rev 0.xls | [13 empty] | With Scaling | Using F1, F2 & F3 Coefficients |  |  | With Scaling
ERCOT | ERCOT |  | CNP | CNP |  | PELCAR | Primary | Total | Total |  |  | 2016 | Secondary | 2016 | 2016 | 2016 | 2016 | 2016 | Total | 2016 | Adjustment for % Losses |  | 2008 | 2008
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | Total Losses | DLF | DLF | Primary Loss % | Primary Loss % | Sec | Pri | Primary MW Losses | Sec MW Losses
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | Secondary | Primary
SIEL | [15 empty] | 0% |  |  |  | 0%
|  |  |  | 50 | 20.6358 | 29.3642 | 0.00098244 | 20.6368 | 41.27% | 29.3632 | 149.1754 | -119.8122 | 0.0050883 | 169.8173 | 339.6% | 339.6%
|  |  |  | 135 | 20.6387 | 114.3613 | 0.014902 | 20.6536 | 15.3% | 114.3464 | 149.1805 | -34.8341 | 0.00043011 | 169.8345 | 125.8% | 125.8%
|  |  |  | 500 | 20.6805 | 479.3195 | 0.26177 | 20.9423 | 4.188% | 479.0577 | 149.2715 | 329.7862 | 0.038551 | 170.2523 | 34.05% | 34.05%
1299.803 | 5199.2121 |  | 250 | 1000 | 20.816 | 979.184 | 1.0924 | 21.9084 | 2.191% | 978.0916 | 149.5772 | 828.5144 | 0.24331 | 171.7289 | 17.17% | 17.17%
3119.5272 | 12478.109 | 1 | 600 | 2400 | 21.6756 | 2378.3244 | 6.4449 | 28.1205 | 1.172% | 2371.8795 | 151.5401 | 2220.3394 | 1.7475 | 181.408 | 7.559% | 7.559% | 7.052% | 0.7202% | 1.172% | 1.172% |  |  | 28.1205 | 181.408
3639.4485 | 14557.7938 | 2 | 700 | 2800 | 22.0512 | 2777.9488 | 8.7927 | 30.8439 | 1.102% | 2769.1561 | 152.3988 | 2616.7573 | 2.4271 | 185.6698 | 6.631% | 6.631% | 6.222% | 0.7311% | 1.102% | 1.102% |  |  | 30.8439 | 185.6698
4159.3697 | 16637.4787 | 3 | 800 | 3200 | 22.4846 | 3177.5154 | 11.504 | 33.9886 | 1.062% | 3166.0114 | 153.389 | 3012.6224 | 3.217 | 190.5946 | 5.956% | 5.956% | 5.623% | 0.7545% | 1.062% | 1.062% |  |  | 33.9886 | 190.5946
4679.2909 | 18717.1635 | 4 | 900 | 3600 | 22.9758 | 3577.0242 | 14.5786 | 37.5545 | 1.043% | 3562.4455 | 154.5104 | 3407.9352 | 4.1167 | 196.1815 | 5.449% | 5.449% | 5.176% | 0.7862% | 1.043% | 1.043% |  |  | 37.5545 | 196.1815
5199.2121 | 20796.8483 | 5 | 1000 | 4000 | 23.5248 | 3976.4752 | 18.0164 | 41.5413 | 1.039% | 3958.4587 | 155.7625 | 3802.6962 | 5.1257 | 202.4294 | 5.061% | 5.061% | 4.836% | 0.8237% | 1.039% | 1.039% |  |  | 41.5413 | 202.4294
5719.1333 | 22876.5332 | 6 | 1100 | 4400 | 24.1316 | 4375.8684 | 21.8173 | 45.9489 | 1.044% | 4354.0511 | 157.1449 | 4196.9062 | 6.2435 | 209.3373 | 4.758% | 4.758% | 4.574% | 0.8654% | 1.044% | 1.044% |  |  | 45.9489 | 209.3373
6239.0545 | 24956.218 | 7 | 1200 | 4800 | 24.7962 | 4775.2038 | 25.981 | 50.7772 | 1.058% | 4749.2228 | 158.6573 | 4590.5655 | 7.4696 | 216.9041 | 4.519% | 4.519% | 4.37% | 0.9103% | 1.058% | 1.058% |  |  | 50.7772 | 216.9041
6758.9757 | 27035.9028 | 8 | 1300 | 5200 | 25.5186 | 5174.4814 | 30.5075 | 56.026 | 1.077% | 5143.974 | 160.2991 | 4983.6749 | 8.8037 | 225.1289 | 4.329% | 4.329% | 4.211% | 0.9577% | 1.077% | 1.077% |  |  | 56.026 | 225.1289
7278.8969 | 29115.5877 | 9 | 1400 | 5600 | 26.2987 | 5573.7013 | 35.3965 | 61.6952 | 1.102% | 5538.3048 | 162.07 | 5376.2348 | 10.2453 | 234.0104 | 4.179% | 4.179% | 4.088% | 1.007% | 1.102% | 1.102% |  |  | 61.6952 | 234.0104
7798.8181 | 31195.2725 | 10 | 1500 | 6000 | 27.1366 | 5972.8634 | 40.6478 | 67.7845 | 1.13% | 5932.2155 | 163.9695 | 5768.246 | 11.7938 | 243.5479 | 4.059% | 4.059% | 3.993% | 1.058% | 1.13% | 1.13% |  |  | 67.7845 | 243.5479
8318.7393 | 33274.9573 | 11 | 1600 | 6400 | 28.0324 | 6371.9676 | 46.2615 | 74.2939 | 1.161% | 6325.7061 | 165.9973 | 6159.7088 | 13.4489 | 253.7401 | 3.965% | 3.965% | 3.921% | 1.11% | 1.161% | 1.161% |  |  | 74.2939 | 253.7401
8838.6605 | 35354.6422 | 12 | 1700 | 6800 | 28.9859 | 6771.0141 | 52.2372 | 81.2231 | 1.194% | 6718.7769 | 168.1529 | 6550.624 | 15.2101 | 264.5861 | 3.891% | 3.891% | 3.867% | 1.163% | 1.194% | 1.194% |  |  | 81.2231 | 264.5861
9358.5817 | 37434.327 | 13 | 1800 | 7200 | 29.9972 | 7170.0028 | 58.5748 | 88.572 | 1.23% | 7111.428 | 170.4359 | 6940.9921 | 17.077 | 276.0849 | 3.835% | 3.835% | 3.83% | 1.217% | 1.23% | 1.23% | 0 | 0 | 88.572 | 276.0849
9878.503 | 39514.0118 | 14 | 1900 | 7600 | 31.0663 | 7568.9337 | 65.2742 | 96.3405 | 1.268% | 7503.6595 | 172.8458 | 7330.8136 | 19.049 | 288.2354 | 3.793% | 3.805% | 3.806% | 1.271% | 1.268% | 1.28% | 1 | 1 | 97.2525 | 289.1474
10398.4242 | 41593.6967 | 15 | 2000 | 8000 | 32.1932 | 7967.8068 | 72.3353 | 104.5284 | 1.307% | 7895.4716 | 175.3824 | 7720.0892 | 21.1257 | 301.0366 | 3.763% | 3.787% | 3.793% | 1.327% | 1.307% | 1.331% | 2 | 2 | 106.4484 | 302.9566
10918.3454 | 43673.3815 | 16 | 2100 | 8400 | 33.3778 | 8366.6222 | 79.7577 | 113.1356 | 1.347% | 8286.8644 | 178.0451 | 8108.8193 | 23.3068 | 314.4874 | 3.744% | 3.78% | 3.789% | 1.382% | 1.347% | 1.383% | 3 | 3 | 116.1596 | 317.5114
11438.2666 | 45753.0663 | 17 | 2200 | 8800 | 34.6203 | 8765.3797 | 87.5415 | 122.1618 | 1.388% | 8677.8382 | 180.8335 | 8497.0047 | 25.5917 | 328.587 | 3.734% | 3.782% | 3.794% | 1.439% | 1.388% | 1.436% | 4 | 4 | 126.3858 | 332.811
11958.1878 | 47832.7511 | 18 | 2300 | 9200 | 35.9206 | 9164.0794 | 95.6864 | 131.6069 | 1.431% | 9068.3931 | 183.7473 | 8884.6458 | 27.98 | 343.3342 | 3.732% | 3.792% | 3.807% | 1.495% | 1.431% | 1.491% | 5 | 5 | 137.1269 | 348.8542
12478.109 | 49912.436 | 19 | 2400 | 9600 | 37.2786 | 9562.7214 | 104.1922 | 141.4709 | 1.474% | 9458.5291 | 186.786 | 9271.7432 | 30.4712 | 358.7281 | 3.737% | 3.809% | 3.825% | 1.552% | 1.474% | 1.546% | 6 | 6 | 148.3829 | 365.6401
12998.0302 | 51992.1208 | 20 | 2500 | 10000 | 38.6944 | 9961.3056 | 113.0589 | 151.7534 | 1.518% | 9848.2466 | 189.9492 | 9658.2974 | 33.065 | 374.7676 | 3.748% | 3.832% | 3.849% | 1.61% | 1.518% | 1.602% | 7 | 7 | 160.1534 | 383.1676
13517.9514 | 54071.8056 | 21 | 2600 | 10400 | 40.168 | 10359.832 | 122.2863 | 162.4544 | 1.562% | 10237.5456 | 193.2365 | 10044.3091 | 35.7608 | 391.4517 | 3.764% | 3.86% | 3.879% | 1.667% | 1.562% | 1.658% | 8 | 8 | 172.4384 | 401.4357
14037.8726 | 56151.4905 | 22 | 2700 | 10800 | 41.6995 | 10758.3005 | 131.8742 | 173.5736 | 1.607% | 10626.4264 | 196.6475 | 10429.7789 | 38.5583 | 408.7794 | 3.785% | 3.893% | 3.912% | 1.725% | 1.607% | 1.715% | 9 | 9 | 185.2376 | 420.4434
14557.7938 | 58231.1753 | 23 | 2800 | 11200 | 43.2887 | 11156.7113 | 141.8224 | 185.111 | 1.653% | 11014.889 | 200.1818 | 10814.7072 | 41.4569 | 426.7497 | 3.81% | 3.93% | 3.95% | 1.783% | 1.653% | 1.773% | 10 | 10 | 198.551 | 440.1897
15077.715 | 60310.8601 | 24 | 2900 | 11600 | 44.9356 | 11555.0644 | 152.1308 | 197.0664 | 1.699% | 11402.9336 | 203.8389 | 11199.0946 | 44.4563 | 445.3616 | 3.839% | 3.971% | 3.991% | 1.841% | 1.699% | 1.831% | 11 | 11 | 212.3784 | 460.6736
15597.6362 | 62390.545 | 25 | 3000 | 12000 | 46.6404 | 11953.3596 | 162.7992 | 209.4396 | 1.745% | 11790.5604 | 207.6185 | 11582.9418 | 47.556 | 464.6141 | 3.872% | 4.016% | 4.035% | 1.9% | 1.745% | 1.889% | 12 | 12 | 226.7196 | 481.8941
16117.5575 | 64470.2298 | 26 | 3100 | 12400 | 48.403 | 12351.597 | 173.8276 | 222.2305 | 1.792% | 12177.7695 | 211.5202 | 11966.2493 | 50.7555 | 484.5063 | 3.907% | 4.063% | 4.082% | 1.958% | 1.792% | 1.948% | 13 | 13 | 241.5745 | 503.8503
16637.4787 | 66549.9146 | 27 | 3200 | 12800 | 50.2233 | 12749.7767 | 185.2156 | 235.4389 | 1.839% | 12564.5611 | 215.5435 | 12349.0175 | 54.0545 | 505.037 | 3.946% | 4.114% | 4.131% | 2.017% | 1.839% | 2.007% | 14 | 14 | 256.9429 | 526.541
17157.3999 | 68629.5995 | 28 | 3300 | 13200 | 52.1015 | 13147.8985 | 196.9632 | 249.0647 | 1.887% | 12950.9353 | 219.6881 | 12731.2472 | 57.4525 | 526.2053 | 3.986% | 4.166% | 4.183% | 2.076% | 1.887% | 2.067% | 15 | 15 | 272.8247 | 549.9653
17677.3211 | 70709.2843 | 29 | 3400 | 13600 | 54.0374 | 13545.9626 | 209.0702 | 263.1076 | 1.935% | 13336.8924 | 223.9535 | 13112.9389 | 60.9491 | 548.0102 | 4.029% | 4.221% | 4.237% | 2.134% | 1.935% | 2.127% | 16 | 16 | 289.2196 | 574.1222
18197.2423 | 72788.9691 | 30 | 3500 | 14000 | 56.0311 | 13943.9689 | 221.5365 | 277.5676 | 1.983% | 13722.4324 | 228.3394 | 13494.0931 | 64.5438 | 570.4508 | 4.075% | 4.279% | 4.293% | 2.193% | 1.983% | 2.187% | 17 | 17 | 306.1276 | 599.0108
18717.1635 | 74868.654 | 31 | 3600 | 14400 | 58.0826 | 14341.9174 | 234.3618 | 292.4444 | 2.031% | 14107.5556 | 232.8453 | 13874.7103 | 68.2362 | 593.5259 | 4.122% | 4.338% | 4.351% | 2.253% | 2.031% | 2.247% | 18 | 18 | 323.5484 | 624.6299
19237.0847 | 76948.3388 | 32 | 3700 | 14800 | 60.1919 | 14739.8081 | 247.5461 | 307.738 | 2.079% | 14492.262 | 237.4708 | 14254.7912 | 72.0259 | 617.2347 | 4.171% | 4.399% | 4.411% | 2.312% | 2.079% | 2.307% | 19 | 19 | 341.482 | 650.9787
19757.0059 | 79028.0236 | 33 | 3800 | 15200 | 62.359 | 15137.641 | 261.0891 | 323.4481 | 2.128% | 14876.5519 | 242.2155 | 14634.3363 | 75.9125 | 641.5762 | 4.221% | 4.461% | 4.472% | 2.371% | 2.128% | 2.368% | 20 | 20 | 359.9281 | 678.0562
20276.9271 | 81107.7085 | 34 | 3900 | 15600 | 64.5839 | 15535.4161 | 274.9908 | 339.5747 | 2.177% | 15260.4253 | 247.0791 | 15013.3462 | 79.8955 | 666.5493 | 4.273% | 4.525% | 4.534% | 2.43% | 2.177% | 2.429% | 21 | 21 | 378.8867 | 705.8613
20796.8483 | 83187.3933 | 35 | 4000 | 16000 | 66.8665 | 15933.1335 | 289.2509 | 356.1175 | 2.226% | 15643.8825 | 252.0611 | 15391.8214 | 83.9745 | 692.153 | 4.326% | 4.59% | 4.598% | 2.49% | 2.226% | 2.49% | 22 | 22 | 398.3575 | 734.393
21706.7104 | 86826.8418 |  | 4175 | 16700 | 71.0002 | 16628.9998 | 315.0683 | 386.0685 | 2.312% | 16313.9315 | 261.0634 | 16052.8681 | 91.3424 | 738.4743 | 4.422% | 4.698% | 4.712% | 2.594% | 2.312% | 2.588% | 23 | 23
9898 | 39592 |  | 1903.75 | 7615 |  | 7615
15 min | ERCOT |  | 15 min | CNP |  | 7584 | AAL for CNP (7,584 MW) is measured at the Dist Fdr Bkr (PELCAR - Column G) so this value is increased 31 MW (Cell F24 ) for the high side of the sub trfs | [9 empty] | Secondary | Primary | CenterPoint Energy
9898 | 39592 | AAL | 1903.75 | 7615 | 31.1075 | 7583.8925 | 65.5325 | 96.64 | 1.269% | 7518.36 | 172.9387 | 7345.4213 | 19.125 | 288.7037 | 3.791% |  | 3.805% | 1.274% | At ERCOT AAL
17852.25 | 71409 | Peak | 3865 | 15460 | 63.7986 | 15396.2014 | 270.0844 | 333.883 | 2.16% | 15126.117 | 245.3634 | 14880.7536 | 78.4905 | 657.7369 | 4.254% |  | 4.256% | 2.154% | At ERCOT Peak
| 1.8036 |  |  | 2.0302 |  | 15460
[6 empty] | 15395 | Peak for CNP (15,395 MW) is measured at the Dist Fdr Bkr (PELCAR - Column G) so this value is increased 65 MW (Cell F44) for the high side of the sub trfs
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % Losses above AAL are scaled proportionately ---> | [14 empty] | Scaling for % Losses |  |  | 2017
(When ERCOT is at peak, CNP is 4 intervals below peak, so % losses at ERCOT peak are scaled up to match % losses at CNP peak.) | [14 empty] | Secondary | Primary |  | For Secondary Distribution Customers "D"
|  |  |  | Substation Transformers |  | Primary Conductor |  |  |  | Distribution Transformers |  | Secondary Conductor |  |  | 0.18% | 0.18% |  | Secondary Constants
|  |  |  | B Constant | A Constant | B Constant | A Constant |  |  | B Constant | A Constant | B Constant | A Constant
|  |  | 2016 Values ----> | 20.6354 | 1.8059e-07 | 0 | 1.1394e-06 |  |  | 149.175 | 4.204e-07 | 0 | 3.5446e-07 | <--- 2016 Values
|  |  | 2015 Values ----> | 20.867 | 1.7797e-07 | 0 | 1.1394e-06 |  |  | 145.39 | 4.3561e-07 | 0 | 3.5446e-07 | <--- 2015 Values
|  |  | 2014 Values ----> | 19.863 | 1.893e-07 | 0 | 1.1394e-06 |  |  | 142.346 | 4.4856e-07 | 0 | 3.5446e-07 | <--- 2014 Values
|  |  | 2013 Values ----> | 19.473 | 1.9548e-07 | 0 | 1.1394e-06 |  |  | 137.751 | 4.7391e-07 | 0 | 3.5446e-07 | <--- 2013 Values
|  |  | 2012 Values ----> | 21.1118 | 1.8286e-07 | 0 | 1.1394e-06 |  |  | 133.986 | 5.0407e-07 | 0 | 3.5446e-07 | <--- 2012 Values
|  |  | 2009 Values ----> | 20.312 | 1.9194e-07 | 0 | 1.1394e-06 |  |  | 130.794 | 5.041e-07 | 0 | 3.5446e-07 | <--- 2009 Values
|  |  | 2008 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2008 Values |  |  | F1 = | 0.01684 | right
|  |  | 2007 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2007 Values |  |  | F2 = | 0.00096 | middle
[17 empty] | F3 = | 0.02025 | left
|  |  |  | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | <--- 1995 |  | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | <--- 1995
|  |  |  | 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2001 |  | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2001 |  |  |  | For Primary Distribution Customers "E"
|  |  |  | 20.2955 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2004/2006 |  | 133.2966 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2004/2006 |  |  |  | Primary Constants
|  |  |  | 2.866% increase in Sub Trf nameplate MVA from 2001 to 2004 | [5 empty] | 15.9% 1ncrease in distribution trf nameplate KVA from 2001 to 2004
|  |  | 2007 Start Values ----> | 18.586 | 2.13e-07 | 0 | 1.1116e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <---2007 Start Value |  |  | F1 = | 0.01157 | right
|  |  |  | New values as per updated |  | Add 2.5 % to 2006 values due |  |  |  | New values as per updated | [6 empty] | F2 = | 6.5e-05 | middle
|  |  | 2007 Adjustments ----> | substation trf review. |  | to increased loading on circuits |  |  |  | distribution trf review. | [6 empty] | F3 = | 0.0011 | left
|  |  |  | Decrease from 2006 values. |  | as per revised Design Criteria |  |  |  | Decrease from 2006 values. |  | No change to 2006 values.
[11 empty] | AAL for ERCOT (15 mins) = 9,898 |  |  | DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
(See graphs below and to the right)
2017
Secondary Constants
F1 = | 0.01684 | right
F2 = | 0.00096 | middle
F3 = | 0.02025 | left

## 3) Loss Equations
System Loss Equations For CenterPoint Energy for 2017 DLF
| Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
Substation Transformers
| 78.919 = | A * (17,965*17,965) + 20.635 |  |  |  |  | 78.9194
| A = | 1.8059e-07 |  |  |  |  | 20.6354
| B = | 20.6354 | Total No-Load Losses For Substation Transformers = 20.635 MW |  |  |  | 58.284
Total Load Losses = 58.284 MW at 17,965 MW load level (Sub Trf base name plate rating)
[6 empty] | 2016 for use in 2017 | 17965
[5 empty] | No Load Losses | 20.6354 | 17965
[5 empty] | Load Losses | 58.284 | 322741225
[5 empty] | Total | 78.9194
1.8059e-07
Primary Conductor
| A = | 1.1394e-06
| B = | 0
Distribution Transformers
| 245.286 = | A * (15,120*15,120) + 149.175
| A = | 4.204e-07 | Total Load Losses = 96.110 MW at 15,120 MW input to Dist Trfs
| B = | 149.175 | Total No-Load Losses For Distribution Transformers = 149.175 MW |  |  |  |  | 245.2856
|  |  |  | 2016 | Corresponds to CNP load at Dist Bkrs of 15,395.00 MW (coincident peak) |  |  | 149.175
|  | No Load Losses |  | 149.175 | Corresponds to CNP load at high side of sub trfs of 15,460 MW |  |  | 96.1106
|  | Load Losses |  | 96.1106 | Corresponds to CNP load input to distribution service trfs of 15,120.00
|  | Total |  | 245.2856 |  |  |  | 15120
15120
|  |  |  | Information from: DLF - 2016 Dist Trf Summary for DLF Calculation Rev 10 12 2016.xlsx |  |  |  | 228614400
Secondary Conductor | [7 empty] | 4.204e-07
| A = | 3.5446e-07
| B = | 0

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified