## Slide 1
ERCOT Black Start Enhancements
Sandip Sharma
Manager, Operations Planning
01/12/2017

## Slide 2: Overview
  Current Black-Start Procurement Process
  Issues with Current Procurement Process
  Proposed Improvements

## Slide 3: What is Black-Start Service
Black Start is the procedure to recover from a total or partial shutdown of the transmission system which has caused an extensive loss of supplies.
  The Black Start generator is required to provide start up power to other power stations as the system restoration progresses and will eventually be required to synchronize to other power islands.
In the event of a Black Start, the service requires the provider to:
  Start up its main generator(s),
  Carry out in coordination with the TDSP initial energization of sections of the Transmission System and distribution network, and,
  Support sufficient demand to create and control a stable power island.
The Black Start Service (BSS) is procured from generators that have the capability to start main blocks of generation from an on-site auxiliary generator, without reliance on external site supplies.

## Slide 4: Current Black Start Service Procurement
Objective
  Select a group of Black Start capable resources that meets all of the Black Start selection criteria with minimum cost based upon the response to ERCOT RFP.
  Selection criteria includes
    Analysis of Bids using MATLAB program (multiple runs)
    Simulated restoration of near peak load (68,500 MW)
    Proximity to load centers/nuclear power plants/gas pipelines
      Expected restoration of off-site power to nuclear units within 4 hours
    Availability of strong transmission network (restoration corridors)
Biennial procurement process
Up to 18 black start units procured in the past
Most recent procurement cycle procured 14 units

## Slide 5: Nexant Study - Issues with Current Process
Reduced interest in BSS contracts. Reasons for reduced interest in bidding for Black Start contracts –
  Prohibitive entry/set-up costs
  Topology Changes
  Prohibitive costs of NERC CIP compliance, etc.
No clear reasoning for the number of islands employed other than historical and the number of procured resources
Non-optimizing analysis tools for BSS
  Non-optimized Black Start cranking sequence
  Lack of power flow solution in BSS analysis tool
Potentially procure unit that are in unhelpful location
Biennial selections are same due to limited number of bids
Two year contract is insufficient time for units to recover the cost of adding Black-Start capability

## Slide 6: Nexant Study - Proposed Improvements
Defining islands in a way that leads to faster load recovery rather than in reaction to unit selection. Items to consider –
  Load centers
  Proximity to nuclear power plant
  System topology
  If islands cross TSP boundaries, coordination requirements
  Sync-check relay locations
Conducting a Black Start Capability study of the system with the aim of generating a ranking of resources.
Use an optimizing software to determine the cranking sequence in coordination with the TSPs
  Optimal Black Start Capability (OBC) tool from Electric Power Research Institute (EPRI)
  Select primary and alternative Black Start units based on locations
  Valid power flow solution of intermediate system states with no violations
Implement incentives for resources willing to participate in Black-Start Service
  Changing the black start (BS) procurement cycle to a longer period to allow for better confidence in return on investment.

## Slide 7: Next Steps
Complete system restoration studies with all potential resources to short list the most optimal set(s) of black start units for each island.
Publish the study results and the list of resources
File NPRR to change the procurement cycle

## Slide 8
Questions?