## Slide 1
Far West Texas Transmission Project -
ERCOT Independent Review Update
January 24, 2017

## Slide 2: Overview
AEPSC and Oncor jointly submitted Far West Texas Project (FWTP) for Regional Planning Group review. This is a Tier 1 project that is estimated to cost $ 423 million.
  Proposed for 2021 to 2022 timeframe
  Addresses oil and gas related load forecasts
  Reliability Issues
    Voltage Collapse
    Loss of Load
    Short-Circuit Strength & System Protection
  Provide Operational Flexibility
  Provides future upgrade path for Far West Region

## Slide 3: Far West Texas Project
Source: AEP/ONCOR RPG submittal on 21-Apr-2016 (http://www.ercot.com/calendar/2016/4/21/81733-RPG)

## Slide 4: Study Assumptions
1. Base Case
  Constructed from 16RTP reliability case 16RTP_2021_SUM_WFW
  Study Region consists of Far-West and West Weather Zones
  Generator additions that meet Planning Guide Section 6.9 criteria in study region were added to the case (2016 October GIS report).
  Transmission Projects expected to be in-service within the study region by 2021 at the time of the study were added to the case
  Applied 2021 oil and gas related load forecasts
    Culberson loop: 426 MW
    Barilla Junction Area lines: ~ 511 MW
  N-1 SCOPF Dispatch
  2. No Solar Case
    Base Case with solar units turned off in West and Far west regions (Total available solar ~ 1341 MW)
    N-1 SCOPF Dispatch

## Slide 5: Steady State Analysis – Preliminary Results
Contingency Analysis was performed on the starting cases
P-1 and P-7 contingencies related to the study region were considered
Voltage deviations, voltage violations and thermal violations were monitored
Notes: Unsolved contingencies . Look into it.

## Slide 6: Preliminary Results – Thermal Violations
Post Contingency thermal violation
  Monitor all transmission lines and transformers in study region (excl. GSU)
    Use Rate A for Normal Conditions
    Use Rate B for Emergency Conditions
Overloaded Element | Zone | kV | Length, in mi | Worst Case Overload, in % | 
 |  |  |  | Base Case | No Solar Case
Cosden to Big Spring SW - ckt1 | FW | 138 | 1.0 | - | 100.6
Rio Pecos to Woodward 2 - ckt1 | FW | 138 | 1.9 | - | 104.5
Rio Pecos to Woodward 1 tap - ckt1 | FW | 138 | 2.2 | - | 103.8
Woodward 2 to 16th St TNP - ckt1 | FW | 138 | 31.8 | - | 114.0
Woodward 1 tap to Tombstone - ckt1 | FW | 138 | 15.7 | - | 105.1

## Slide 7: Preliminary Results – Voltage Violations
      Post Contingency voltage deviations > 8% on non-radial load buses
      NONE
Post Contingency voltage violation criteria
Monitor all buses 100 kV and above
      0.95 < 1.05 Normal
      0.90 < 1.05 Emergency
Bus Name | Bus kV | Zone | Base Case | No Solar Case
ALAMITO CREEK | 138 | Far West | - | 0.897
OXY CENTURY TNP | 138 | Far West | - | 0.893
COUNTY RD 101 TNP | 138 | Far West | - | 0.899
Notes: Incl only far west areas

## Slide 8: Preliminary Results - Dynamic Analysis
2022 DWG dynamic data set case for Culberson Loop
2018 HWLL dynamic data set case for the Barilla Junction area
Voltage stability issues identified in the Culberson loop area under N-1 conditions
No stability issues identified in the Barilla Junction area under N-1 conditions

## Slide 9: Next Steps
  Complete the Steady State and Dynamic stability analysis
  Identify and evaluate project alternatives
  Sensitivity Analysis
    Higher Culberson Loop Load
    PGRR0042-Generator additions with Signed Interconnection Agreements that DO NOT meet Planning Guide Section 6.9 criteria in study region
  Tentative Timeline
    Complete the EIR review – March RPG

## Slide 10
?