## Introduction
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## 2016_Transmission_Losses
TRANSMISSION LOSS FACTORS for 2016 as of 11/24/15
Data from Seasonal SSWG Base Cases Updated with updates received by 11/24/15
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN (9) NOIE INTERNAL TOTAL |  |  |  |  | CPS (5) NOIE INTERNAL TOTAL |  |  |  |  | COG (20) NOIE INTERNAL TOTAL |  |  |  |  | GEUS (21) NOIE INTERNAL TOTAL |  |  |  |  | COD (19) NOIE INTERNAL TOTAL |  |  |  |  | BPUB (15) NOIE INTERNAL TOTAL |  |  |  |  | BTU (22) NOIE INTERNAL TOTAL |  |  |  |  | COCS (23) NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 2016_SPG1 | 66281.7 | 64858.8 | 1294.67 | 1412.41 | 1143 | 2469 | 40.71 | 41.3 | 1367.3 | 2942 | 4285 | 27.2 | 31.3 | 1374.3 | 140 | 354.5 | 2.37 | 2.4 | 216.9 | 41 | 61.5 | 0.19 | 0.2 | 20.7 | 0 | 337.3 | 0.83 | 0.8 | 338.1 | 104 | 256.3 | 0.63 | 0.7 | 153 | 110 | 363.5 | 3.39 | 3.9 | 257.4 | 0 | 142 | 0.24 | 0.2 | 142.2
Spring Off Peak | 2016_SPG2 | 41202.4 | 40467.8 | 665.25 | 723.96 | 82 | 1465 | 19.17 | 19.4 | 1402.4 | 1089 | 2228 | 9.23 | 10.1 | 1149.1 | 52.6 | 157.8 | 0.42 | 0.4 | 105.6 | 26 | 38.7 | 0.07 | 0.1 | 12.8 | 0 | 209.1 | 0.41 | 0.4 | 209.5 | 104 | 265.6 | 0.61 | 0.7 | 162.3 | 43.4 | 322.3 | 2.18 | 2.3 | 281.2 | 0 | 74.6 | 0.21 | 0.2 | 74.8
Summer On Peak | 2016_SUM1 | 80559.6 | 78875.5 | 1518.91 | 1662.35 | 1137 | 2787 | 49.51 | 50.8 | 1700.8 | 4367.2 | 5078 | 35.94 | 42.8 | 753.6 | 304.3 | 517 | 6.38 | 6.4 | 219.1 | 91 | 104 | 0.67 | 0.7 | 13.7 | 0 | 374.8 | 1.04 | 1 | 375.8 | 104 | 284.1 | 0.72 | 0.8 | 180.9 | 266 | 402 | 4.82 | 5.8 | 141.8 | 0 | 204.2 | 0.21 | 0.2 | 204.4
Summer Off Peak | 2016_SUM2 | 49194.9 | 48448.8 | 665.42 | 735.27 | 100 | 1495 | 15.12 | 15.1 | 1410.1 | 1501.1 | 2742 | 8.34 | 9.5 | 1250.4 | 51.7 | 156.9 | 0.85 | 0.9 | 106.1 | 91 | 63.5 | 0.35 | 0.3 | -27.2 | 0 | 191.2 | 0.45 | 0.4 | 191.6 | 104 | 291.2 | 0.74 | 0.8 | 188 | 42.4 | 255.7 | 1.73 | 1.7 | 215 | 0 | 94.9 | 0.15 | 0.1 | 95
Fall On Peak | 2016_FAL1 | 65886.2 | 64639.5 | 1118.58 | 1235.92 | 975 | 2331 | 35.86 | 36.7 | 1392.7 | 2839.3 | 4136 | 27.26 | 31.2 | 1327.9 | 103.2 | 318.2 | 2.24 | 2.2 | 217.2 | 49 | 89.5 | 0.37 | 0.4 | 40.9 | 0 | 302.9 | 0.57 | 0.6 | 303.5 | 104 | 272 | 0.63 | 0.7 | 168.7 | 110 | 303.6 | 2.88 | 3.4 | 197 | 0 | 170.3 | 0.24 | 0.2 | 170.5
Fall Off Peak | 2016_FAL2 | 41893.6 | 41221 | 601.28 | 661.83 | 0 | 1514.2 | 17.2 | 17.2 | 1531.4 | 2641.2 | 2399 | 14.49 | 18 | -224.2 | 32.2 | 137.5 | 0.41 | 0.4 | 105.7 | 34 | 55.8 | 0.15 | 0.1 | 21.9 | 0 | 127.2 | 0.23 | 0.2 | 127.4 | 104 | 235.5 | 0.45 | 0.5 | 132 | 43.4 | 202.5 | 1.2 | 1.2 | 160.3 | 0 | 91.9 | 0.08 | 0.1 | 92
Winter On Peak | 2017_WIN1 | 67825.9 | 66164.8 | 1517.74 | 1649.46 | 735 | 1992 | 37.64 | 38.2 | 1295.2 | 3611.6 | 4070 | 23.83 | 29 | 487.4 | 189 | 403 | 2.88 | 2.9 | 216.9 | 0 | 72.2 | 0.18 | 0.2 | 72.4 | 0 | 232.4 | 0.71 | 0.7 | 233.1 | 104 | 232.2 | 0.48 | 0.6 | 128.8 | 110 | 334.4 | 4.52 | 5 | 229.4 | 0 | 146 | 0.22 | 0.2 | 146.2
Winter Off Peak | 2017_WIN2 | 48039.8 | 47164.7 | 786.61 | 864.03 | 550 | 1628 | 20.66 | 20.8 | 1098.8 | 2431.1 | 2930 | 16.93 | 20.3 | 519.2 | 55 | 164.7 | 0.82 | 0.8 | 110.5 | 0 | 42.4 | 0.06 | 0.1 | 42.5 | 0 | 118.5 | 0.25 | 0.3 | 118.8 | 104 | 292.8 | 0.68 | 0.8 | 189.6 | 12 | 273.6 | 2.62 | 2.6 | 264.2 | 0 | 74.2 | 0.15 | 0.1 | 74.3
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 2016_SPG1 | 2480 | 1281.65 | 460 | 76.1 | 113 | 0 | 4410.75 |  | 8269.1 | 3869.9 | 4399.2 | 75.56 | 2016_SPG1
Spring Off Peak | 2016_SPG2 | 2480 | 1098.66 | 460 | 26.4 | 113 | 0 | 4178.06 |  | 4761.1 | 3397.7 | 1363.4 | 32.3 | 2016_SPG2
Summer On Peak | 2016_SUM1 | 2480 | 1143.56 | 460 | 40 | 113 | 0 | 4236.56 |  | 9751.1 | 3590.1 | 6161 | 99.29 | 2016_SUM1
Summer Off Peak | 2016_SUM2 | 2480 | 1098.66 | 460 | 1.4 | 113 | 0 | 4153.06 |  | 5290.4 | 3429 | 1861.4 | 27.73 | 2016_SUM2
Fall On Peak | 2016_FAL1 | 2480 | 1138.6 | 460 | 76.5 | 113 | 0 | 4268.1 |  | 7923.5 | 3818.4 | 4105.1 | 70.05 | 2016_FAL1
Fall Off Peak | 2016_FAL2 | 2480 | 1139.52 | 460 | 26.4 | 113 | 0 | 4218.92 |  | 4763.6 | 1946.5 | 2817.1 | 34.21 | 2016_FAL2
Winter On Peak | 2017_WIN1 | 2480 | 1138.65 | 460 | 68.8 | 113 | 0 | 4260.45 |  | 7482.2 | 2809.4 | 4672.8 | 70.46 | 2017_WIN1
Winter Off Peak | 2017_WIN2 | 2480 | 1138.65 | 460 | 62.1 | 113 | 0 | 4253.75 |  | 5524.2 | 2417.9 | 3106.3 | 42.17 | 2017_WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 61870.95 | 37024.34 | 2.093% | 1.797% |  | 2469 | 1465 | 1.622% | 1.292% |  | 4285 | 2228 | 0.6308% | 0.4126% |  | 354.5 | 157.8 | 0.6641% | 0.2655% |  | 61.5 | 38.7 | 0.308% | 0.1806% |  | 337.3 | 209.1 | 0.2455% | 0.1957% |  | 256.3 | 265.6 | 0.2452% | 0.2291% |  | 363.5 | 322.3 | 0.924% | 0.6718% |  | 142 | 74.6 | 0.1687% | 0.2807%
SUMMER | 76323.04 | 45041.84 | 1.99% | 1.477% |  | 2787 | 1495 | 1.745% | 1.001% |  | 5078 | 2742 | 0.7028% | 0.3032% |  | 517 | 156.9 | 1.219% | 0.5388% |  | 104 | 63.5 | 0.6401% | 0.5482% |  | 374.8 | 191.2 | 0.2767% | 0.2348% |  | 284.1 | 291.2 | 0.2528% | 0.2535% |  | 402 | 255.7 | 1.185% | 0.672% |  | 204.2 | 94.9 | 0.1027% | 0.1578%
FALL | 61618.1 | 37674.68 | 1.815% | 1.596% |  | 2331 | 1514.2 | 1.515% | 1.123% |  | 4136 | 2399 | 0.6548% | 0.6004% |  | 318.2 | 137.5 | 0.699% | 0.2973% |  | 89.5 | 55.8 | 0.4117% | 0.2681% |  | 302.9 | 127.2 | 0.1878% | 0.1805% |  | 272 | 235.5 | 0.2311% | 0.1907% |  | 303.6 | 202.5 | 0.9397% | 0.5891% |  | 170.3 | 91.9 | 0.1407% | 0.08698%
WINTER | 63565.45 | 43786.05 | 2.388% | 1.796% |  | 1992 | 1628 | 1.855% | 1.253% |  | 4070 | 2930 | 0.5821% | 0.5745% |  | 403 | 164.7 | 0.7096% | 0.4954% |  | 72.2 | 42.4 | 0.2487% | 0.1413% |  | 232.4 | 118.5 | 0.3046% | 0.2105% |  | 232.2 | 292.8 | 0.2063% | 0.2317% |  | 334.4 | 273.6 | 1.334% | 0.9485% |  | 146 | 74.2 | 0.1505% | 0.2017%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC
SPRING | 1.1903e-05 | 1.3561 |  |  |  | 0.00032915 | 0.80942 |  |  |  | 0.00010608 | 0.17622 |  |  |  | 0.0020267 | -0.054362 |  |  |  | 0.0055895 | -0.03576 |  |  |  | 0.00038824 | 0.11451 |  |  |  | -0.0017269 | 0.68782 |  |  |  | 0.0061199 | -1.3006 |  |  |  | -0.0016615 | 0.40466
SUMMER | 1.6392e-05 | 0.739 |  |  |  | 0.00057601 | 0.1401 |  |  |  | 0.00017104 | -0.16576 |  |  |  | 0.0018888 | 0.24247 |  |  |  | 0.0022703 | 0.404 |  |  |  | 0.00022827 | 0.19116 |  |  |  | 9.655e-05 | 0.22536 |  |  |  | 0.0035049 | -0.22418 |  |  |  | -0.00050391 | 0.20563
FALL | 9.1618e-06 | 1.2508 |  |  |  | 0.00047984 | 0.39658 |  |  |  | 3.1318e-05 | 0.52524 |  |  |  | 0.0022233 | -0.0084032 |  |  |  | 0.0042614 | 0.03031 |  |  |  | 4.1754e-05 | 0.17518 |  |  |  | 0.0011059 | -0.069713 |  |  |  | 0.0034679 | -0.11314 |  |  |  | 0.00068564 | 0.023965
WINTER | 2.9889e-05 | 0.48774 |  |  |  | 0.0016521 | -1.4365 |  |  |  | 6.6661e-06 | 0.55496 |  |  |  | 0.0008987 | 0.34739 |  |  |  | 0.0036033 | -0.01147 |  |  |  | 0.00082573 | 0.11268 |  |  |  | 0.00041931 | 0.10893 |  |  |  | 0.0063344 | -0.78456 |  |  |  | -0.00071435 | 0.25475
EFFECTIVE DATES | SEASON
03/01/2016 - 05/31/2016 | SPRING
06/01/2016 - 09/30/2016 | SUMMER
10/01/2016 - 11/30/2016 | FALL
12/01/2016 - 02/28/2017 | WINTER