## Introduction
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## 2017_Transmission_Losses
TRANSMISSION LOSS FACTORS for 2017 as of 11/18/16
Data from Seasonal SSWG Base Cases Updated with updates received by 11/18/16
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN (9) NOIE INTERNAL TOTAL |  |  |  |  | CPS (5) NOIE INTERNAL TOTAL |  |  |  |  | COG (20) NOIE INTERNAL TOTAL |  |  |  |  | GEUS (21) NOIE INTERNAL TOTAL |  |  |  |  | COD (19) NOIE INTERNAL TOTAL |  |  |  |  | BPUB (15) NOIE INTERNAL TOTAL |  |  |  |  | BTU (22) NOIE INTERNAL TOTAL |  |  |  |  | COCS (23) NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 2017_SPG1 | 66013.6 | 64567.2 | 1330.19 | 1435.25 | 1122 | 2498 | 39.18 | 40.5 | 1416.5 | 5471.6 | 3904 | 37.05 | 44.3 | -1523.3 | 228.8 | 417.1 | 3.24 | 3.2 | 191.5 | 41 | 62.7 | 0.23 | 0.2 | 21.9 | 0 | 337.9 | 0.8 | 0.8 | 338.7 | 60 | 293.2 | 0.88 | 0.9 | 234.1 | 12 | 341.9 | 4.68 | 4.7 | 334.6 | 0 | 147 | 0.21 | 0.2 | 147.2
Spring Off Peak | 2017_SPG2 | 41567.8 | 40762.8 | 737.38 | 793.86 | 1122 | 1386 | 26.06 | 27.5 | 291.5 | 2922.1 | 2147 | 11.54 | 14.1 | -761 | 110.1 | 200.7 | 0.94 | 0.9 | 91.5 | 34 | 42.1 | 0.11 | 0.1 | 8.2 | 0 | 354.5 | 0.46 | 0.5 | 355 | 60 | 145.5 | 0.28 | 0.3 | 85.8 | 12 | 179.5 | 1.84 | 1.8 | 169.3 | 0 | 66.6 | 0.03 | 0 | 66.6
Summer On Peak | 2017_SUM1 | 82264.3 | 80509.6 | 1594.13 | 1716.59 | 1530.7 | 2831.5 | 58.35 | 60 | 1360.8 | 4985 | 5162 | 37.65 | 44.2 | 221.2 | 310 | 544.9 | 7.4 | 7.4 | 242.3 | 91 | 107 | 0.78 | 0.8 | 16.8 | 0 | 342.5 | 1.07 | 1.1 | 343.6 | 104 | 304.1 | 0.69 | 0.8 | 200.9 | 257 | 442.1 | 4.95 | 5.8 | 190.9 | 0 | 213 | 0.23 | 0.2 | 213.2
Summer Off Peak | 2017_SUM2 | 49924.4 | 48997.7 | 852.06 | 915.27 | 988 | 1558 | 30.03 | 31 | 601 | 3027.5 | 2787 | 12.92 | 15.8 | -224.7 | 102.3 | 181.7 | 1.57 | 1.6 | 81 | 91 | 66.9 | 0.4 | 0.4 | -23.7 | 0 | 191.7 | 0.33 | 0.3 | 192 | 58 | 160.5 | 0.24 | 0.2 | 102.7 | 67.4 | 226.7 | 1.91 | 2 | 161.3 | 0 | 97.4 | 0.04 | 0 | 97.4
Fall On Peak | 2017_FAL1 | 68348.3 | 66696.9 | 1529.58 | 1640.01 | 1121 | 2339.1 | 45.69 | 47 | 1265.1 | 5555.2 | 4379 | 36.72 | 44.2 | -1132 | 207.1 | 367.4 | 3.05 | 3.1 | 163.4 | 49 | 83.5 | 0.39 | 0.4 | 34.9 | 0 | 303.5 | 0.66 | 0.7 | 304.2 | 58 | 289.9 | 0.83 | 0.8 | 232.7 | 12 | 423.5 | 7.92 | 8 | 419.5 | 0 | 192.5 | 0.43 | 0.4 | 192.9
Fall Off Peak | 2017_FAL2 | 42238.7 | 41217.6 | 948.19 | 1009.54 | 720.8 | 1402.8 | 45.31 | 45.8 | 727.8 | 2375 | 2190 | 11.12 | 13.1 | -171.9 | 97.8 | 173.1 | 0.88 | 0.9 | 76.2 | 26 | 49.2 | 0.13 | 0.1 | 23.3 | 0 | 127.3 | 0.17 | 0.2 | 127.5 | 58 | 135.9 | 0.22 | 0.2 | 78.1 | 43.4 | 214.3 | 3.06 | 3.3 | 174.2 | 0 | 82.3 | 0.03 | 0 | 82.3
Winter On Peak | 2018_WIN1 | 68859.3 | 67221.9 | 1515.53 | 1625.96 | 1126 | 2070.4 | 46.13 | 47.4 | 991.8 | 4990.7 | 3959 | 33.61 | 40.1 | -991.6 | 280.9 | 463.9 | 4.81 | 4.8 | 187.8 | 0 | 82.1 | 0.29 | 0.3 | 82.4 | 0 | 174.7 | 0.64 | 0.6 | 175.3 | 69 | 284.1 | 0.83 | 0.8 | 215.9 | 12 | 336.4 | 4.74 | 4.8 | 329.2 | 0 | 146 | 0.26 | 0.3 | 146.3
Winter Off Peak | 2018_WIN2 | 48871.7 | 47692 | 1093.9 | 1168.15 | 858 | 1621.9 | 47.14 | 48.1 | 812 | 3313.3 | 2573 | 14.74 | 18 | -722.3 | 123.1 | 219.1 | 1.59 | 1.6 | 97.6 | 0 | 65.4 | 0.18 | 0.2 | 65.6 | 0 | 89.3 | 0.26 | 0.3 | 89.6 | 69 | 187.4 | 0.37 | 0.4 | 118.8 | 0 | 228.1 | 2.79 | 2.8 | 230.9 | 0 | 72.2 | 0.06 | 0.1 | 72.3
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 2017_SPG1 | 2721 | 1068.59 | 612.47 | 26.32 | 113 | 0 | 4541.38 |  | 8001.8 | 1161.2 | 6840.6 | 86.27 | 2017_SPG1
Spring Off Peak | 2017_SPG2 | 2721 | 996.99 | 612.47 | 13.82 | 113 | 0 | 4457.28 |  | 4521.9 | 306.9 | 4215 | 41.26 | 2017_SPG2
Summer On Peak | 2017_SUM1 | 2721 | 1334.5 | 363.47 | 23.2 | 113 | 0 | 4555.17 |  | 9947.1 | 2789.7 | 7157.4 | 111.12 | 2017_SUM1
Summer Off Peak | 2017_SUM2 | 2721 | 993.08 | 612.47 | 6.02 | 113 | 0 | 4445.57 |  | 5269.9 | 987 | 4282.9 | 47.44 | 2017_SUM2
Fall On Peak | 2017_FAL1 | 2721 | 988.59 | 612.47 | 60.55 | 113 | 0 | 4495.61 |  | 8378.4 | 1480.7 | 6897.7 | 95.69 | 2017_FAL1
Fall Off Peak | 2017_FAL2 | 2721 | 988.59 | 612.47 | 4.24 | 113 | 0 | 4439.3 |  | 4374.9 | 1117.5 | 3257.4 | 60.92 | 2017_FAL2
Winter On Peak | 2018_WIN1 | 2721 | 980.19 | 567.93 | 46.64 | 113 | 0 | 4428.76 |  | 7516.6 | 1137.1 | 6379.5 | 91.31 | 2018_WIN1
Winter Off Peak | 2018_WIN2 | 2721 | 936.97 | 567.93 | 31.62 | 113 | 0 | 4370.52 |  | 5056.4 | 764.5 | 4291.9 | 67.13 | 2018_WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 61472.22 | 37110.52 | 2.164% | 1.987% |  | 2498 | 1386 | 1.544% | 1.846% |  | 3904 | 2147 | 0.9401% | 0.5346% |  | 417.1 | 200.7 | 0.7708% | 0.4662% |  | 62.7 | 42.1 | 0.3655% | 0.2606% |  | 337.9 | 354.5 | 0.2362% | 0.1296% |  | 293.2 | 145.5 | 0.2992% | 0.1921% |  | 341.9 | 179.5 | 1.35% | 1.015% |  | 147 | 66.6 | 0.1427% | 0.04502%
SUMMER | 77709.13 | 45478.83 | 2.051% | 1.874% |  | 2831.5 | 1558 | 2.019% | 1.891% |  | 5162 | 2787 | 0.7241% | 0.4614% |  | 544.9 | 181.7 | 1.34% | 0.8567% |  | 107 | 66.9 | 0.7237% | 0.5944% |  | 342.5 | 191.7 | 0.3114% | 0.1718% |  | 304.1 | 160.5 | 0.2264% | 0.1493% |  | 442.1 | 226.7 | 1.107% | 0.8355% |  | 213 | 97.4 | 0.1079% | 0.04105%
FALL | 63852.69 | 37799.4 | 2.395% | 2.508% |  | 2339.1 | 1402.8 | 1.916% | 3.129% |  | 4379 | 2190 | 0.8316% | 0.5052% |  | 367.4 | 173.1 | 0.8233% | 0.5058% |  | 83.5 | 49.2 | 0.4649% | 0.2635% |  | 303.5 | 127.3 | 0.217% | 0.1334% |  | 289.9 | 135.9 | 0.2855% | 0.1616% |  | 423.5 | 214.3 | 1.836% | 1.408% |  | 192.5 | 82.3 | 0.2229% | 0.03644%
WINTER | 64430.54 | 44501.18 | 2.352% | 2.458% |  | 2070.4 | 1621.9 | 2.18% | 2.824% |  | 3959 | 2573 | 0.8418% | 0.5696% |  | 463.9 | 219.1 | 1.026% | 0.7205% |  | 82.1 | 65.4 | 0.352% | 0.2745% |  | 174.7 | 89.3 | 0.365% | 0.2903% |  | 284.1 | 187.4 | 0.2913% | 0.197% |  | 336.4 | 228.1 | 1.389% | 1.208% |  | 146 | 72.2 | 0.1778% | 0.08303%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC
SPRING | 7.2616e-06 | 1.7175 |  |  |  | -0.00027095 | 2.2211 |  |  |  | 0.00023078 | 0.039131 |  |  |  | 0.0014077 | 0.18365 |  |  |  | 0.0050914 | 0.046252 |  |  |  | -0.006422 | 2.4062 |  |  |  | 0.00072558 | 0.086498 |  |  |  | 0.0020669 | 0.64366 |  |  |  | 0.0012143 | -0.035847
SUMMER | 5.5189e-06 | 1.6225 |  |  |  | 0.0001006 | 1.7343 |  |  |  | 0.00011059 | 0.15323 |  |  |  | 0.0013304 | 0.61493 |  |  |  | 0.0032255 | 0.37857 |  |  |  | 0.00092565 | -0.0055985 |  |  |  | 0.00053674 | 0.063163 |  |  |  | 0.0012617 | 0.54945 |  |  |  | 0.00057797 | -0.015244
FALL | -4.3371e-06 | 2.6724 |  |  |  | -0.0012955 | 4.9463 |  |  |  | 0.0001491 | 0.17867 |  |  |  | 0.0016342 | 0.22293 |  |  |  | 0.0058706 | -0.025305 |  |  |  | 0.00047461 | 0.072947 |  |  |  | 0.00080433 | 0.052314 |  |  |  | 0.0020459 | 0.96937 |  |  |  | 0.0016918 | -0.1028
WINTER | -5.316e-06 | 2.6947 |  |  |  | -0.0014378 | 5.1564 |  |  |  | 0.00019639 | 0.064298 |  |  |  | 0.001249 | 0.44681 |  |  |  | 0.0046413 | -0.02907 |  |  |  | 0.00087467 | 0.2122 |  |  |  | 0.00097466 | 0.014397 |  |  |  | 0.0016721 | 0.82696 |  |  |  | 0.0012836 | -0.0096448
EFFECTIVE DATES | SEASON
03/01/2017 - 05/31/2017 | SPRING
06/01/2017 - 09/30/2017 | SUMMER
10/01/2017 - 11/30/2017 | FALL
12/01/2017 - 02/28/2018 | WINTER