## Slide 1
Maximum Shadow Prices in RUC:
Initial Results
QSE Managers Working Group
Market Analysis
January 30, 2017

## Slide 2: Introduction
Resources were RUC-committed after 283 HRUCs in 2016
107 of these HRUCs have been rerun twice
  Once using the current RUC maximum shadow price values
  Once using the current SCED maximum shadow price values
The results of each HRUC were then compared using five metrics
Constraint Category | Maximum Shadow Price ($/MWh) |  | Ratio
 | Current RUC | SCED | 
Base case or voltage violation | 1,000,000 | 5,000 | 200
345 kV contingency | 1,000,000 | 4,500 | 222
138 kV contingency | 900,000 | 3,500 | 257
69 kV contingency | 700,000 | 2,800 | 250

## Slide 3: Metrics Compared
Recommended Resource-hours
Energy injected by LSLs of RUC-recommended Resources
Startup plus minimum generation costs of RUC-recommended Resources
Total transmission constraint violations remaining in RUC solutions
Hours of violations above certain thresholds

## Slide 4: Caveats
The following slides present the output recommendations from the RUC Engine, not what was actually committed by ERCOT Operators
  These slides will use the term “RUC-recommended” rather than “RUC-committed”
The graphs on the following slides are independently ordered by the current RUC results, so the HRUC represented in a position on one slide does not correspond to the same position on other slides.

## Slide 5: Recommended Resource-Hours
64 HRUCs had fewer recommended resource-hours
40 had the same number
3 had more
23 had exactly the same recommendations

## Slide 6: LSL Energy of RUC-Recommended Resources
64 HRUCs had less total LSL energy
36 had the same amount
7 had more

## Slide 7: Startup and Minimum Generation Costs
70 HRUCs had lower total startup and minimum generation costs
34 had the same amount
3 had more

## Slide 8: Transmission Violations in RUC Solution
Note that the two graphs have different y-axis scales
2 HRUCs had lower total MWh of transmission violations
34 had the same amount
71 had more

## Slide 9: Constraint-Hours Above 100% of Limit
1 HRUC had fewer constraint-hours above 100% of the limit
36 had the same number
70 had more

## Slide 10: Constraint-Hours Above 105% of Limit
2 HRUCs had fewer constraint-hours above 105% of the limit
75 had the same number
30 had more

## Slide 11: Constraint-Hours Above 110% of Limit
3 HRUCs had fewer constraint-hours above 110% of the limit
89 had the same number
15 had more

## Slide 12: Constraint-Hours Above 120% of Limit
3 HRUCs had fewer constraint-hours above 120% of the limit
101 had the same number
3 had more

## Slide 13: Results Summary
Metric | Maximum Shadow Prices ($/MWh) |  | Change
 | Current RUC | SCED | 
Recommended Resource-Hours | 2,455 | 1,889 | -23%
Startup Costs ($1000s) | 4,538 | 2,576 | -43%
Min Gen Costs ($1000s) | 6,673 | 4,243 | -36%
Startup Plus Min Gen Costs ($1000s) | 11,211 | 6,820 | -39%
LSL Energy (MWh) | 108,202 | 76,010 | -30%
Total Violation (MWh) | 19,891 | 20,683 | +4%
Constraint-hours above 100% of Limit | 795 | 1,041 | +31%
Constraint-hours above 105% of Limit | 432 | 483 | +12%
Constraint-hours above 110% of Limit | 246 | 274 | +11%
Constraint-hours above 120% of Limit | 89 | 90 | +1%

## Slide 14: Comments and Next Steps
These are initial results presented for discussion purposes
More analysis and discussion is needed to determine whether changes are both acceptable and warranted
ERCOT will continue to analyze the issue
  Compare recommendations to actual commitments
  Perform additional analysis of current results
  Complete rerunning the set of 283 HRUCs in 2016
  Analyze reliability impacts
  If warranted, analyze additional maximum shadow price limits