| PGRR Number | 057 | PGRR Title | Responsibilities for Performing Geomagnetic Disturbance (GMD) Vulnerability Assessments |
| --- | --- | --- | --- |
| Date Posted | February 6, 2017 |
| Requested Resolution | Normal |
| Planning Guide Sections Requiring Revision | 3.1.1.5, GMD Vulnerability Assessment (new) 3.1.8, GMD Vulnerability Assessment Development Process (new) 6.11, Process for Developing Geomagnetically-Induced Current (GIC) System Models |
| Related Documents Requiring Revision/Related Revision Requests | None |
| Revision Description | This Planning Guide Revision Request (PGRR) aligns the Planning Guides with North American Electric Reliability Corporation (NERC) Reliability Standard TPL-007-1, Transmission System Planned Performance for Geomagnetic Disturbance Events, by identifying responsibilities for performing studies needed to complete Geomagnetic Disturbance (GMD) vulnerability assessments. |
| Reason for Revision | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |
| Business Case | This PGRR satisfies NERC Reliability Standard TPL-007-1. |

| Sponsor |
| --- |
| Name | Ben Richardson |
| E-mail Address | ben.richardson@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4505 |
| Cell Number |  |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |
| --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

Comments

In order to meet the requirements of NERC TPL-007-1, ERCOT and Market Participants will continue to work jointly to develop the implementation schedule for this PGRR.  To facilitate discussion, ERCOT provides the PGDTF-proposed timeline below for further discussion at PGDTF meetings:

Identify Individual and Joint Responsibilities (PGRR057)

- To be completed by 7/1/17

- NERC enforceable date: 7/1/17

Determine GIC Flow Information to be used for the transformers thermal assessment (Paragraphs (1) and (2) of Section 3.1.8)

- To be completed by 7/1/18

- NERC enforceable date: 1/1/19

Perform Thermal Assessment for Transformers Experiencing ≥75 A GIC (Paragraph (2) of Section 3.1.8)

- To be completed by 7/1/19

- NERC enforceable date: 1/1/21

Determine System Steady State Voltage Criteria for System Performance (Paragraph (3) of Section 3.1.8)

- To be completed by 7/1/19

- NERC enforceable date: 1/1/22

Corrective Action Plan (Paragraphs (4)(a) and (5) of Section 3.1.8)

- To be completed by 7/1/19

- NERC enforceable date: 1/1/22

Complete GMD Vulnerability Assessment every 60 month (Section 3.1.1.5 and paragraph (4) of Section 3.1.8)

- To be completed by 7/1/19

- NERC enforceable date: 1/1/22

Proposed Guide Language Revision

### 3.1.1.5 	Geomagnetic Disturbance (GMD) Vulnerability Assessment

(1)	The purpose of the Geomagnetic Disturbance (GMD) vulnerability assessment is to provide a coordinated transmission plan for the ERCOT System to meet ERCOT and NERC GMD reliability performance criteria for a GMD event.  The most recent Geomagnetically-Induced Current (GIC) system models developed and maintained by ERCOT in conjunction with the TSPs and Resource Entities as described in Section 6.11, Process for Developing Geomagnetically-Induced Current (GIC) System Models, shall be used as the basis for the ERCOT GMD vulnerability assessment.  Projects that are included in the GMD vulnerability assessment are not considered to have been endorsed by ERCOT until they have undergone the appropriate level of RPG Project Review as outlined in Protocol Section 3.11.4, Regional Planning Group Project Review Process, if required.  The process used by ERCOT to develop the GMD vulnerability assessment is outlined in Section 3.1.8, Geomagnetic Disturbance (GMD) Vulnerability Assessment Development Process.

## 3.1.8 	Geomagnetic Disturbance (GMD) Vulnerability Assessment Development Process

- At least once every 60 calendar months ERCOT shall employ the GIC system models described in Section 6.11, Process for Developing Geomagnetically-Induced Current (GIC) System Models, to perform simulations to identify maximum effective GIC flow in the transformers for the worst case geoelectric field orientation for the benchmark GMD event.  ERCOT shall make the maximum effective GIC flows in the transformers available to TSPs and Resource Entities by posting this data on the ERCOT MIS Secure Area.

- Upon written request from the TSP or Resource Entity who owns a transformer within the ERCOT planning area that is included in the ERCOT GIC system models, ERCOT shall perform simulations to make effective GIC time series available no later than 90 calendar days after ERCOT’s receipt of such written requests.

- Each TSP and Resource Entity that owns a transformer(s) within the ERCOT planning area shall perform transformer thermal impact assessments as required in the applicable NERC Reliability Standard and shall provide to ERCOT any suggested actions to mitigate the impact of GICs on its transformers.

- ERCOT shall develop for approval by the Technical Advisory Committee (TAC) criteria for acceptable steady-state voltage performance during the benchmark GMD event.

- ERCOT in conjunction with the TSPs shall perform the ERCOT GMD vulnerability assessment as required in the applicable NERC Reliability Standard.

(a)	ERCOT and the TSPs shall develop corrective action plan(s) as required in the applicable NERC Reliability Standard and document the corrective action plan(s) in the GMD vulnerability assessment.

- ERCOT shall post the GMD vulnerability assessment on the ERCOT MIS Secure Area.

[PGRR046: Insert Section 6.11 below upon system implementation of RRGRR009:] 6.11 Process for Developing Geomagnetically-Induced Current (GIC) System Models (1) To adequately simulate Geomagnetic Disturbance (GMD) events, it is necessary to establish and maintain GIC system models and conduct geomagnetic disturbance vulnerability assessments to determine whether the ERCOT System can withstand performance requirements of the benchmark geomagnetic disturbance event described in North American Electric Reliability Corporation (NERC) Reliability Standards. These models, known as GIC base cases, shall contain appropriate system data, and shall represent projected system conditions that provide a starting point for the required year(s). (a) Transmission Service Providers (TSPs) and ERCOT shall develop the GIC base cases. These base cases are derived from the steady-state base cases developed by Steady-State Working Group (SSWG) for the near-term transmission planning horizon to ensure consistency between the system topology in the SSWG base cases and GIC system models. (b) Each TSP, or its Designated Agent, shall provide its respective transmission network GIC model data in accordance with the GIC System Model Procedure Manual. (c) Each Resource Entity, or its Designated Agent, shall provide its respective Resource Entity-owned generating units, plants, transmission lines, shunt devices and Generation Step Ups (GSUs) connected to the ERCOT System in accordance with the GIC System Model Procedure Manual and the Resource Registration Glossary. (d) ERCOT shall aggregate the GIC system model data supplied by each TSP and Resource Entity and shall compile and maintain the GIC system models. Upon completion of compiling the data for the GIC base cases, ERCOT shall post these cases on the ERCOT Market Information System (MIS) Certified Transmission Service Provider Information page for review and comments as described in the GIC System Model Procedure Manual. (e) Guidelines and formats for the GIC system model data and model maintenance can be found in the GIC System Model Procedure Manual. (f) GIC data is considered Protected Information pursuant to Protocol Section 1.3, Confidentiality. (2) Each TSP and Resource Entity shall provide to ERCOT and update at least once every 60 calendar months a list of Reactive Power compensation devices and other transmission facilities removed as a result of protection system operation or misoperation due to harmonics during a GMD event as described in the applicable NERC Reliability Standard.