| PGRR Number | 057 | PGRR Title | Responsibilities for Performing Geomagnetic Disturbance (GMD) Vulnerability Assessments |
| --- | --- | --- | --- |
| Date Posted | February 6, 2017 |
| Requested Resolution | Normal |
| Planning Guide Sections Requiring Revision | 3.1.1.5, GMD Vulnerability Assessment (new) 3.1.8, GMD Vulnerability Assessment Development Process (new) 6.11, Process for Developing Geomagnetically-Induced Current (GIC) System Models |
| Related Documents Requiring Revision/Related Revision Requests | None |
| Revision Description | This Planning Guide Revision Request (PGRR) aligns the Planning Guides with North American Electric Reliability Corporation (NERC) Reliability Standard TPL-007-1, Transmission System Planned Performance for Geomagnetic Disturbance Events, by identifying responsibilities for performing studies needed to complete Geomagnetic Disturbance (GMD) vulnerability assessments. |
| Reason for Revision | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |
| Business Case | This PGRR satisfies Requirement 1 NERC Reliability Standard TPL-007-1. |

| Sponsor |
| --- |
| Name | Ben Richardson |
| E-mail Address | ben.richardson@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4505 |
| Cell Number |  |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |
| --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

Comments

In order to meet the requirements of NERC TPL-007-1, ERCOT and Market Participants will continue to work jointly to develop the implementation schedule for this PGRR.  To facilitate discussion, ERCOT provides the PGDTF-proposed timeline below for further discussion at PGDTF meetings:

Identify Individual and Joint Responsibilities (PGRR057)

- To be completed by 7/1/17

- NERC enforceable date: 7/1/17

Determine GIC Flow Information to be used for the transformers thermal assessment (Paragraphs (1) and (2) of Section 3.1.8)

- To be completed by 7/1/18

- NERC enforceable date: 1/1/19

Perform Thermal Assessment for Transformers Experiencing ≥75 A GIC (Paragraph (2) of Section 3.1.8)

- To be completed by 7/1/19

- NERC enforceable date: 1/1/21

Determine System Steady State Voltage Criteria for System Performance (Paragraph (3) of Section 3.1.8)

- To be completed by 7/1/19

- NERC enforceable date: 1/1/22

Corrective Action Plan (Paragraphs (4)(a) and (5) of Section 3.1.8)

- To be completed by 7/1/19

- NERC enforceable date: 1/1/22

Complete GMD Vulnerability Assessment every 60 month (Section 3.1.1.5 and paragraph (4) of Section 3.1.8)

- To be completed by 7/1/19

- NERC enforceable date: 1/1/22

Proposed Guide Language Revision

### 3.1.1.5 	Geomagnetic Disturbance (GMD) Vulnerability Assessment

(1)	The purpose of the Geomagnetic Disturbance (GMD) vulnerability assessment is to provide a coordinated transmission plan and corrective action plan(s) for the ERCOT System to meet ERCOT and NERC GMD reliability performance criteria for a GMD event.  The most recent Geomagnetically-Induced Current (GIC) system models developed and maintained by ERCOT in conjunction with the TSPs and Resource Entities as described in Section 6.11, Process for Developing Geomagnetically-Induced Current (GIC) System Models, shall be used as the basis for the ERCOT GMD vulnerability assessment. Projects that are included in the corrective action plan(s) are not considered to have been endorsed by ERCOT until they have undergone the appropriate level of RPG Project Review as outlined in Protocol Section 3.11.4, Regional Planning Group Project Review Process, if required.   Future Tier 1, 2, and 3 projects that have not yet undergone the appropriate level of Regional Planning Group (RPG) Project Review as outlined in Protocol Section 3.11.4, Regional Planning Group Project Review Process, and have not been endorsed by ERCOT will not be included in the GIC system models.  Future Generation Resources that have met the criteria for inclusion in the SSWG system models as defined in Section 6.9, Addition of Proposed Generation Resources to the Planning Models, will be included in the GIC system models. The process used by ERCOT to  perform the GMD vulnerability assessment and corrective action plan(s) is outlined in Section 3.1.8, Geomagnetic Disturbance (GMD) Vulnerability Assessment Development Process.

## 3.1.8 	Geomagnetic Disturbance (GMD) Vulnerability Assessment Development Process

- As required in the applicable NERC Reliability Standard, ERCOT in conjunction with the TSPs shall employ the GIC system models described in Section 6.11, Process for Developing Geomagnetically-Induced Current (GIC) System Models, to perform simulations to identify maximum effective GIC flows and reactive power losses in the high side wye-grounded transformers for the worst case geoelectric field orientation in the ERCOT Region for the benchmark GMD event.  ERCOT shall make the maximum effective GIC flows and reactive power losses in the transformers available to TSPs and Resource Entities by posting this data on the ERCOT MIS Secure Area.   ERCOT shall make the GIC system models and other models used for the GMD vulnerability assessment available to the TSPs upon request.

- Upon written request from the TSP or Resource Entity who owns a high side wye-grounded transformer within the ERCOT planning area that is included in the ERCOT GIC system models, ERCOT shall perform simulations to make effective GIC time series available no later than 90 calendar days after ERCOT’s receipt of such written requests.

- Each TSP and Resource Entity that owns a high side wye-grounded transformer(s) within the ERCOT planning area shall perform transformer thermal impact assessments as required in the applicable NERC Reliability Standard and shall provide to ERCOT any suggested ctionto mitigate the impact of GICs on its transformers.

- In the event a TSP or Resouce Entity has site specific geophysical electric field modeling and/or available GMD/GIC sensing equipment providing it real-time data, such data may be substituted for the worst case geoelectric data provided by ERCOT or NERC as the benchmark GMD event data to be used for determining any requirement to perform applicable transformer thermal impact assessments.

- ERCOT inconjunction with the TSPs and the TSPs shall develop for approval by the Technical Advisory Committee (TAC) criteria for acceptable steady-state voltage performance during the benchmark GMD event.

- ERCOT in conjunction with the TSPs shall perform the ERCOT GMD vulnerability study and assessment as required in the applicable NERC Reliability Standard.

- ERCOT and the TSPs shall develop corrective action plan(s) as required in the applicable NERC Reliability Standard and document the corrective action plan(s)..

- ERCOT and the TSPs shall develop corrective action plan(s) as required in the applicable NERC Reliability Standard and document the corrective action plan(s)developed during the GMD vulnerability assessment in the assessment report.

- ERCOT and the TSPs shall develop corrective action plan(s) as required in the applicable NERC Reliability Standard and document the corrective action plan(s) in the GMD vulnerability assessment.

- ERCOT shall post the GMD vulnerability assessment results (or report) and corrective action plan(s) on the ERCOT MIS Secure Area.

- ERCOT in conjunction with the TSPs shall review the effectiveness of the correction action plan in subsequent GMD vulnerability assessments until it is determined that the ERCOT system meets the performance requirements as specified in the applicable NERC Reliability Standard.

[PGRR046: Insert Section 6.11 below upon system implementation of RRGRR009:] 6.11 Process for Developing Geomagnetically-Induced Current (GIC) System Models (1) To adequately simulate Geomagnetic Disturbance (GMD) events, it is necessary to establish and maintain GIC system models and conduct geomagnetic disturbance vulnerability assessments to determine whether the ERCOT System can withstand performance requirements of the benchmark geomagnetic disturbance event described in North American Electric Reliability Corporation (NERC) Reliability Standards. These models, known as GIC base cases, shall contain appropriate system data, and shall represent projected system conditions that provide a starting point for the required year(s). (a) Transmission Service Providers (TSPs) and ERCOT shall develop the GIC base cases. These base cases are derived from the steady-state base cases developed by Steady-State Working Group (SSWG) for the near-term transmission planning horizon to ensure consistency between the system topology in the SSWG base cases and GIC system models. (b) Each TSP, or its Designated Agent, shall provide its respective transmission network GIC model data in accordance with the GIC System Model Procedure Manual. (c) Each Resource Entity, or its Designated Agent, shall provide its respective Resource Entity-owned generating units, plants, transmission lines, shunt devices and Generation Step Ups (GSUs) connected to the ERCOT System in accordance with the GIC System Model Procedure Manual and the Resource Registration Glossary. (d) ERCOT shall aggregate the GIC system model data supplied by each TSP and Resource Entity and shall compile and maintain the GIC system models. Upon completion of compiling the data for the GIC base cases, ERCOT shall post these cases on the ERCOT Market Information System (MIS) Certified Transmission Service Provider Information page for review and comments as described in the GIC System Model Procedure Manual. (e) Guidelines and formats for the GIC system model data and model maintenance can be found in the GIC System Model Procedure Manual. (f) GIC data is considered Protected Information pursuant to Protocol Section 1.3, Confidentiality. (2) Each TSP and Resource Entity shall provide to ERCOT a list of contingencies as described in the applicable NERC Reliability Standard necessary to perform the GMD vulnerability assessment as outlined in Section 3.1.1.5. (2) Each TSP and Resource Entity shall provide to ERCOT a list of Reactive Power compensation devices and other transmission facilities removed as a result of protection system operation or misoperation due to harmonics during a GMD event as described in the applicable NERC Reliability Standard. (2) Each TSP and Resource Entity shall provide to ERCOT a list of contingencies, including those caused by harmonics created by a GMD event, for use in the GMD vulnerability assessment as outlined in Section 3.1.1.5.

# Comments

CNP Comment

CNP, Oncor

Oncor Comment

LCRA Comment: Updated Language: “Projects that are included as a corrective action plan(s) in the GMD vulnerability assessment are not considered to have been endorsed by ERCOT until they have undergone the appropriate level of RPG Project Review as outlined in Protocol Section 3.11.4, Regional Planning Group Project Review Process, if required. “

AEP Comment: Posssibly move to Section 6.11

AEP Comment

Oncor Comment

Oncor Comment: “Let NERC Standard in effect at the time of the assessment set the schedule so revision to the Planning Guide is not required when NERC revises the Standard”

LCRA Comment

CNP, AEP Comment

Oncor Comment

ERCOT Comment: May need more specifics to reduce compliance risk, similar to specificity outlined in Section 6.11 for R2

Oncor Comment

CNP, LCRA Comment

Oncor Comment

BruceWertz

CNP, Oncor, LCRA Comment

May need to move this requirement to where language is regarding reactive losses in vulnerability cases.

Oncor Comment

Oncor Comment

Oncor Comment

Bruce Wertz

AEP, Oncor, LCRA Comment

CNP Comment

AEP Comment: Possibly be more explicit about the study and the assessment.

Oncor Comment: “The NERC Standard considers the corrective action plan to be separate from the vulnerability assessment.”

CNP Comment

AEP Comment in lieu of previous (4)(a)

LCRA Comment: Start new bullet as (5)

AEP Comment

CNP, Oncor Comment

CNP Comment

LCRA Comment: Same as CNP but should be before previous bullet

CNP Comment

CNP Comment

AEP Comment in lieu of (2)

Oncor Comment in lieu of (2): Possibly add this in vulnerability assessment Section