## Slide 1
UFLS Workshop Discussion
Matt Mereness
Director of Compliance
February 20, 2017

## Slide 2: UFLS Discussion outline
Follow-up from TAC Discussion on October 2016
Background on ERCOT Compliance UFLS survey
Examples of issues and questions with handling Load Resources in survey
Differences between Annual Survey and Ops/Planning
Other emerging issues

## Slide 3: Background on UFLS Survey Requirement
ERCOT Compliance coordinates and conducts an annual survey with the TSPs and DSPs to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event as required by table below from Operating Guides 2.6.1(1) Requirements for Under-Frequency Load Shedding:
2016 results were 7.2% / 12.2% / 12.6% for total of 31.23%

## Slide 4: Current Issues with UFLS
ERCOT Compliance has been asked questions (at OWG) that may point to clarifying the assumptions for measurement of UFLS in the survey, as well as emerging operational concerns.
For reference:
NERC Requirements reflect Planning Coordinator shall have a “UFLS program design”
  See Appendix for NERC details
Operating Guide 2.6.1 is the design of ERCOT Automatic Load Shedding
  In effect since zonal Operating Guides in 2010
Issues:
For the survey just reviewed, current OpGuide language reflects the approach of “At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.”
  Survey data collected does not identify or align circuits with Load Resources for exclusion
There has also been some “double-counting” discussions over whether Load Resources that deploy at 59.7 Hz can be counted towards the UFLS response at 59.3Hz
Notes: Weather 5/12/2015 at 11:00 was mild again this year.

## Slide 5: Example
Load 20MW
Load 20MW
Load 20MW
Load 20MW
Load 20MW
LR = 1MW
Current Annual Survey language could imply this methodology:
Actual System Load = 100 MW
#1
#2
#4
#3
#5
LR = 10MW
TDSP
X
X
Survey System Load = 100 – 40 (Feeders with any LR) = 60 MW
TDSP Breaker #1 armed at 59.3 = 20MW shed (20/60 = 33%)
TDSP Breaker #2 armed at 58.9 = 20MW shed (20/60 = 33%)
TDSP Breaker #3 armed at 58.5 = 20MW shed (20/60 = 33%)

## Slide 6: Example
Load 20MW
Load 20MW
Load 20MW
Load 20MW
Load 20MW
LR = 1MW
ERCOT assumption in Planning and Operations:
System Load at 60Hz = 100 MW
#1
#2
#4
#3
#5
LR = 10MW
TDSP
X
X
System Load in EEA3 or 59.7 = 100 – 11MW LR = 89 MW
TDSP Breaker #1 armed at 59.3 = 20MW shed (20/89 = 22%)
TDSP Breaker #2 armed at 58.9 = 20MW shed (20/89 = 22%)
TDSP Breaker #3 armed at 58.5 = 20MW shed (20/89 = 22%)
Load 19MW
----------------
Load 10MW
-----------------

## Slide 7: Emerging Issues and Conclusion
Emerging issues
Because of scenario of UFLS event when in an EEA, ERCOT does not believe double-counting of Load Resources should be allowed for UFLS 5/10/10 performance.
Similar to Load Resources, load amounts that are shed from ERS should also not contribute to UFLS performance.
Distributed Energy Resources are not considered in language at this point.
Conclusion and possible issues to consider resolution to:
Inconsistency in UFLS Survey and Ops/Planning
  Consider addressing exemption of load circuits equipped with Load Resources in survey
Potentially out-of-date language in Protocols and Guides may be worth re-alignment
  Consistent handling of Load Resource and ERS
  Any considerations for DERs

## Slide 8: Appendix- NERC Requirement
NERC standard PRC-006-2 — Automatic Underfrequency Load Shedding:
Requirement 9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. [VRF: High][Time Horizon: Long-term Planning]
Measurement 9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9.

## Slide 9: Appendix- ERCOT Operating Guide
OpGuide 2.6.1 Automatic Firm Load Shedding
At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding. The under-frequency relays shall be set to provide Load relief as follows:
With the assistance of applicable Transmission Service Providers (TSPs), ERCOT will, prior to the peak each year, survey each Distribution Service Provider’s (DSP’s) compliance with the automatic Load shedding steps above, and report its findings to the Technical Advisory Committee (TAC). For minimum compliance, DSPs are obligated to meet the prescribed percent values at all times. It is not permitted to use rounding to meet the minimum. ERCOT will direct a review of the automatic firm Load shedding program whenever warranted by conditions. At a minimum, this review will follow the Reliability and Operations Subcommittee (ROS) directed dynamic simulations of automatic firm Load shedding conducted at five-year intervals beginning in the Summer of 2001.
Additional under-frequency relays may be installed on Transmission Facilities with the approval of ERCOT provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay. A DSP may by mutual agreement arrange to have all or part of its automatic Load shedding requirement performed by another entity. ERCOT will be notified and provided with the details of any such arrangement prior to implementation.

## Slide 10: Appendix- ERCOT Operating Guide
OpGuide 2.6.1 Automatic Firm Load Shedding
(4) DSPs shall ensure, to the extent possible, and under the direction of ERCOT, that Loads equipped with under-frequency relays are dispersed geographically throughout the ERCOT Region to minimize the impact of Load shedding within a given geographical area. Customers equipped with under-frequency relays shall be dispersed without regard to which Load Serving Entity (LSE) serves the customer. DSPs shall ensure that the under-frequency relays connected to each Load will operate with a fixed time delay of no more than 30 cycles. Total time from the time when frequency first reaches one of the values specified above to the time Load is interrupted should be no more than 40 cycles, including all relay and breaker operating times. If the frequency drops below 58.5 Hz, ERCOT shall determine additional steps to continue operation.
(5) If a loss of Load occurs due to the operation of under-frequency relays, a Transmission Operator (TO) designated by a DSP to shed Load may rotate the physical Load interrupted to minimize the duration of interruption experienced by individual Customers or to restore the availability of under-frequency Load-shedding capability. In no event shall the initial total amount of Load without service be decreased by a TO without the approval of ERCOT. TOs, in coordination with DSPs, shall make every reasonable attempt to restore Load, either by automatic or manual means, to preserve system integrity. Restoration of any Load shed by Under-Frequency Load Shedding (UFLS) systems shall be coordinated with ERCOT.
(6) Whenever possible, TOs and DSPs shall not manually drop Load connected to under-frequency relays during the implementation of Level 3 of an Energy Emergency Alert (EEA).