## Slide 1
Reliability Unit Commitment Discussion with QMWG
February 27th, 2017

## Slide 2: Introduction
In late 2016, QMWG requested that ERCOT analyze the potential impacts of lowering shadow price caps used in the RUC engine
During the previous QMWG meeting, initial information from that study were provided looking only at how engine outputs and recommendations would change on an aggregate level
For this presentation, we’ll be discussing how potential reliability concerns are being evaluated along with information about potential concerns being reviewed
Additionally, some other RUC related items are included in the material regarding the other noted agenda items

## Slide 3: Constraints with Increased Violations
The table includes a subset of constraints that were more violated
  Increase is summed violation amount
  Some of theses constraints were already in real-time with historical behavior
Constraint | Summed Violation Amount |  | Max. Increase in Violation Amount | 
 | Current Caps | Lower Caps | Current Caps | Lower Caps
DFL_MAR8 - BETFM_66_A | 17.37 | 33.45 | 1.1% | 5.1%
DFL_MAR8 - BETHK_66_A | 75.27 | 108.66 | 0.0% | 4.7%
DLONWAR5 - FANNIN_VICTOR1_1 | 6.1 | 28.79 | 0.0% | 7.9%
DSN_BFP8 - BAY_SARG_1 | 45.83 | 59.34 | 0.0% | 11.4%
DSNGZEN5 - BETFM_66_A | 0 | 16.17 | 0.0% | 3.1%
DSNGZEN5 - BETHK_66_A | 4.08 | 124.52 | 0.0% | 6.9%
DWH_STP5 - BONIVI_RINCON1_1 | 0 | 6.59 | 0.0% | 8.9%
SBEVASH8 - BIG_COTU_1 | 67.63 | 83.65 | 2.3% | 13.9%
SBREHIG8 - 367T347_1 | 41.09 | 79.98 | 6.3% | 15.3%
SFERZ48 - WEIDER_RAND_1 | 0 | 22.21 | 0.0% | 3.9%
SFTWW_D8 - AIR_W_DE_1 | 38.04 | 81.38 | 0.1% | 3.0%
SJARDIL8 - DIL_COTU_1 | 142.21 | 155.44 | 0.0% | 8.8%
SJMCW_D8 - FTW_W_DE_1 | 176.98 | 198.72 | 0.0% | 2.0%
SNADRIC8 - NAD_ELCM_1 | 1.76 | 14.45 | 0.0% | 9.4%
SSIGSAN8 - NCA_SMTP_1 | 21.66 | 42.6 | 0.0% | 11.0%
SVLDO2W8 - BAY_SARG_1 | 89.91 | 171.31 | 1.6% | 14.1%
XPHR58 - G138_10C_1 | 3.73 | 24.53 | 1.8% | 10.8%
XPHR58 - MDO_AT1 | 4.32 | 46.94 | 0.0% | 2.6%
XPHR58 - MDO_AT1L | 6.04 | 49.11 | 0.0% | 2.8%

## Slide 4: Resources No Longer Recommended
As discussed last time, the change is shadow price cap reduced the number of Resources that were recommended by the RUC engine
This difference includes both Resources that ERCOT eventually committed and others that were not committed for that operating day
For ones committed, a number of the Resources were tied to constraints mentioned on the previous slide
  Currently working with operations on the reliability impacts for these recommendations that were removed

## Slide 5: Example Operating Day – July 10th
2 Resources that were recommended by the RUC engine and committed were no longer recommended with the lower shadow price cap
The noted commitment reason was constraint DRNS_TB5 - SNGZEN99_A however other related constraints were SVLDO2W8 - BAY_SARG_1, SVLDO2W8 - MRK_VNVL_1, and XDOW58 - BAY_SARG_1
  These latter 3 constraints became more violated in the RUC optimization as a result of the change
  For those two Resources, the shift factors were ~-15% for DRNS_TB5 - SNGZEN99_A and ~-1% for the other 3 constraints
No clear alternative solutions provided by the RUC engine with the lower shadow price caps

## Slide 6: Further Analysis
Continuing to analyze the removed commitment recommendations
  Working with Operations to identify issues
  Impacts of increased violations
  Impacts to congestion management in Real-Time
  Individual cases are being reviewed manually
What max. shadow prices will ensure that the acceptable level of reliability is achieved with reduced commitments

## Slide 7: RUC Display Heuristic Rules
There have been questions from QMWG around the heuristic rule for identifying as for “capacity” or “congestion” within the displays
  The logic looks at RUC recommendations and active constraints in the last iteration of RUC
  If a recommended Resource has a shift factor less than -0.1% for any of the active constraints, it was highlighted in the display as for “congestion”
    The value is configurable
  Otherwise identified as for “capacity”
  Shift factor used in rule is same shift factor as is displayed to the Operator
    Historically the single slack bus shift factor, but now the load-distributed slack bus shift factor
  Thinking about “non-shift factor” logic rules as well

## Slide 8: Operator Display Enhancements
In addition to these discussions, we have been looking at ways to give the Operators better information through their displays
1 enhancement just implemented was to provide constraint shift factors based on load-distributed slack bus
  As opposed to the values being based on a single slack bus, which is used for the optimization
  More equivalent to the values seen by Operators during real-time (produced by the Real-Time Contingency Analysis application)
  Provides a better understanding of how the Resource(s) may be used in real-time
Working to identify other improvements

## Slide 9: Extreme Cold Weather Discussion
There were several months of discussion around RUC and extreme cold weather events
Some of the things that resulted from that were:
  NPRR767, Commitment by RUC for Long Lead Time Resource
  Updates to Operator Desk Procedures
    “Increasing Ancillary Services for Extreme Cold Weather” in the Resource Desk Procedures updated in ‘14 and ’16
Believe it can be removed from the Open Action Items list