## Slide 1
Black Start Study Report
ERCOT Staff
ROS
03/02/2017

## Slide 2
Outline
Review of ERCOT’s Black-start Procurement process
  EPRI’s Optimal Black-Start Capability (OBC) tool
Island Definitions
Study Process and Results

## Slide 3: Review of ERCOT Black Start Procurement
Bi-annual RFP requesting offers for black start service
Analysis of offers by ERCOT
  Currently using in-house tool; a heuristic Matlab program.
  No optimization and no power flow solution of system state.
Services to be procured determined based on analysis results
  TOs develop black start plans around these units.
A standard set of performance tests performed by each unit as determined by the Nodal Operating Guides
  Basic black start test, line energization, remote load pick-up; etc.
  Contracts and issuance of certificates

## Slide 4: EPRI Optimal Black-start Capability (OBC) Tool
  Optimization seeks to maximize MWHr, using load MW to keep voltages within limits.
  Uses mixed-integer programming (CPLEX) to optimize generator start-up sequencing and optimal power flow (OPF) to generate a solvable power flow for every step of the calculated sequence.
  Accounts for Ferranti rise effect.
  Simulates load pick-up.
Requires the following information:
  Potential black start unit(s) (have to be identified by the user).
  Representative element switching times, Generator Characteristics (start-up times, ramp rates etc.), Voltage constraints, Simulation time, Load parameters, Line parameters.
  Accepts data in PSS®E RAW file (v30) format.

## Slide 5: EPRI Optimal Black-start Capability (OBC) Tool
  Complexity of the optimization problem limits the size of the island.
  Require solutions in reasonable time.
  Avoid unsolvable formulations of objective function and constraints.
  Define islands that can be analyzed individually
  Reduces the complexity and size of the optimization problem.
  Meets the proposal from NEXANT on having well-defined islands as part of the analysis

## Slide 6: Island Definitions
  Base the islands around load centers as good locations for black start units rather than around bid-in black start units.
  High opportunity for rapid load-pick up.
  Can reach stable island frequency quickly.
  Shorter crew travel times due to load proximity minimizes error in study caused by assumptions made on element switching times.
  Restoration of off-site power to nuclear generation sites, a critical constraint.

## Slide 7: Island Definitions
  Eight islands defined across ERCOT reflects major load centers
  Dallas/Fort Worth
  Central Texas
  Houston
  Corpus Christi
  Valley
  Laredo
  West Texas
  Far West Texas
Some islands split up into two or more sub-islands to meet set constraints.
If BSS candidates found outside the physical island, island definition extended to study external candidate as BSU for that island.

## Slide 8: Study Process
  Determine optimal cranking sequence for any generator when used as a black start resource (CPLEX) and simulate the energizing of the transmission grid and load pick-up (OPF)
Assumptions regarding the system and resources –
  All facilities assumed to be available for determination of optimal sequencing and simulation of restoration actions
  Resources using coal, nuclear, wind and solar power not analyzed in this study for suitability to black start service
  Resources inside Private Use Networks and asynchronous ties (DC, VFT etc.) to neighboring systems also not included in the analysis

## Slide 9: Study Process
  Determine suitability of existing generation resources to black start service from a network restoration perspective.
  No assumptions made about the black start capability of resources.
  Assume for purposes of this study, all resources being tested could be made black start capable
  Two metrics used to evaluate a resource for suitability to black start service
  Maximum energy that can be restored in the island, using the calculated sequence of actions.
  Time taken to develop a stable island that can be the basis for further load restoration.

## Slide 10: Study Results
  Constraints on bus voltage, and active/reactive power balancing applied as part of the OPF formulation
  Bus voltage constraints of 0.9 – 1.1 per unit used as standard for the study.
  When OPF was unsolved, constraints relaxed to 0.8 – 1.2 per unit to check whether issue was sustainability of voltage.
  Scenario deemed unsolved if convergence failed for both standard and relaxed voltage constraints
  Load pick-up simulated using OPF to allow constraints to be met.

## Slide 11: Study Results - Summary
Islands | Sub Islands | # Units tested for BSS | Solved
DFW | DFW West | 22 | √
 | DFW East | 45 | √
Central Texas | Austin | 41 | √
 | San Antonio | 25 | √
Houston | North/Central | 32 | √
 | South (& STP) | 16 | √
Corpus Christi |  | 6 | √
Valley |  | 11 | √
Laredo |  | 8 | √
West Texas |  | 9 | √
Far West Texas |  | 15 | √

## Slide 12: Conclusions
Redefined study approach with load centers as pre-defined targets for stable island formation.
Multiple new units identified with potential to be useful during a black start restoration
  Most of these units have not historically participated in black start service.

## Slide 13
Questions?