## Slide 1
Far West Texas Transmission Project -
ERCOT Independent Review Update
March 21, 2017

## Slide 2: Overview
AEPSC and Oncor jointly submitted Far West Texas Project (FWTP) for Regional Planning Group review. This is a Tier 1 project that is estimated to cost $ 423 million.
  Proposed for 2021 to 2022 timeframe
  Addresses oil and gas related development
    Voltage Collapse
    Loss of Load
    Short-Circuit Strength & System Protection
  Provides Operational Flexibility
  Provides options for 345 kV expansion

## Slide 3: Far West Texas Project
Source: AEP/ONCOR RPG submittal on 21-Apr-2016 (http://www.ercot.com/calendar/2016/4/21/81733-RPG)

## Slide 4: EIR Study Status
Initial Study Case - preliminary findings
  Steady-State violations Pecos County for No Solar Case
  Dynamic stability issues identified in the Culberson loop area under N-1 conditions
Study Base Case Changes
  Significant load increases (contracts signed)
    Initial Study Case added 254 MW Load, latest augments by 134 MW. Total 388 MW over RTP case.
  Changes to non-conforming load identified in Pecos and Reeves Counties
  Following discussions with Oncor and AEP, ERCOT accepted the model changes and agreed to update the base cases (March 2017)

## Slide 5: Next Steps
  Complete Re-study with the updated base case
  Evaluate project alternatives
  Sensitivity Analysis
    Higher Culberson Loop Load
    PGRR0042-Generator additions with Signed Interconnection Agreements that DO NOT meet Planning Guide Section 6.9 criteria in study region
  Tentative Timeline
    EIR update to RPG – April 2017
    Complete the EIR review, present findings to RPG and TAC – May 2017
    Recommendation to ERCOT BOD – June 2017

## Slide 6
?