## Slide 1
Review of Transmission Loss Factors
Technical Advisory Committee
March 23, 2017

## Slide 2: Introduction
ERCOT Protocols Section 13 contains the procedures for the development of forecasted TLFs and the use of TLFs in settlement. These procedures have remained relatively unchanged since Zonal market open in 2001
In late 2016, ERCOT posted forecasted Transmission Loss Factors (TLFs) for the period covering March 1, 2017 through February 28, 2018
The 2017/18 forecasted TLFs were significantly changed from the 2016/17 forecasted TLFs, which prompted questions from several market participants

## Slide 3: Procedures for Determining Forecasted TLFs
TLFs are determined based on the four seasonal SSWG cases for the upcoming year
  On-peak case for each season
  Off-peak case for each season is the minimum load on the same day as the on-peak case for the season
Generator dispatch for each of the eight cases is determined pursuant to Section 4.3.3 of the SSWG Procedure Manual *
* http://www.ercot.com/content/wcm/key_documents_lists/27292/SSWG_Procedure_Manual.Approved_by_ROS_20160203.docx

## Slide 4: 2016/17 and 2017/18 TLFs

## Slide 5: 2016/17 to 2017/18 Changes in TLFs
With the exception of Winter On-Peak, TLFs increased across the board from 2016/17 to 2017/18
The largest increases from 2016/17 to 2017/18 were for the Fall and Winter Off-Peak cases
Examination of these two SSWG cases indicate that the most significant changes affecting the level of transmission losses were a reduction in the 2017/18 cases of approximately 2.9 GW of generation dispatch in the Houston area, compensated by increased generation dispatch across the rest of ERCOT
These changes significantly increased the flows of power across the ERCOT grid and into the Houston area, thereby producing higher overall transmission losses in the 2017/18 cases

## Slide 6: TLFs, Actual Transmission Losses, and Settlement
Forecast TLFs are posted based on the SSWG linear transmission loss function and the ERCOT load forecast
Deemed Actual TLFs are applied in settlement as a component of Adjusted Metered Load (AML) by truing up the SSWG linear transmission loss function to actual ERCOT operational load
Actual transmission losses are not directly accounted for in settlement
  If Actual transmission losses are greater (less) than Deemed Actual transmission losses, the difference will contribute to positive (negative) Unaccounted for Energy (UFE)
  TLFs and UFE are not allocated the same to all loads

## Slide 7: 2016/17 and 2017/18 TLFs

## Slide 8: Actual Transmission Losses
Five minute data from ERCOT State Estimator for February 8 – 28, 2017
These data include generator step-up transformer and PUN losses
Unlike TLFs that assume a 1:1 correlation with load, actual transmission losses during this time do not exhibit correlation with load, but do exhibit correlation with production from generation that is remote from the larger ERCOT load centers

## Slide 9: Next Steps and Questions?
It is possible to measure and incorporate actual transmission losses into real-time settlement
Should ERCOT and stakeholders further explore possible improvements in the accuracy of the accounting for actual transmission losses in the ERCOT system compared to the current, longstanding approach of applying Deemed Actual TLFs?
Other questions?