## Slide 1
UFLS Workshop Discussion #2
Matt Mereness
Director of Compliance
April 20, 2017

## Slide 2: UFLS Discussion outline
Antitrust Admonition
Recap of Workshop #1 Feb 20, 2017
  Background on issues being considered regarding the UFLS Compliance Survey and the Operations/Planning expectations
Review ERCOT NOGRR draft language
Appendix
  NERC requirement excerpt
  UFLS examples
  Potential Load Resource data to provide

## Slide 3: Background on UFLS Survey Requirement
ERCOT Compliance coordinates and conducts an annual survey with the TSPs and DSPs to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event as required by table below from Operating Guides 2.6.1(1) Requirements for Under-Frequency Load Shedding:
2016 results were 7.2% / 12.2% / 12.6% for total of 31.23%

## Slide 4: Current Issues with UFLS
ERCOT Compliance has been asked questions (at OWG) that may point to clarifying the assumptions for measurement of UFLS in the survey, as well as emerging operational concerns.
For reference:
NERC Requirements reflect Planning Coordinator shall have a “UFLS program design”
  See Appendix for NERC details
Operating Guide 2.6.1 is the design of ERCOT Automatic Load Shedding
  In effect since zonal Operating Guides in 2010
Issues:
For the survey just reviewed, current OpGuide language reflects the approach of “At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.”
  Survey data collected does not identify or align circuits with Load Resources for exclusion
There has also been some “double-counting” discussions over whether Load Resources that deploy at 59.7 Hz can be counted towards the UFLS response at 59.3Hz
Notes: Weather 5/12/2015 at 11:00 was mild again this year.

## Slide 5: Key discussion points at last workshop
Consider in 2 phases
  Short-term/Phase 1 address operational risk under ROS
  Longer-term/Phase 2 address emerging issues and market impacts (DERS, ERS, etc)
Short-term/Phase 1:
  Agree the goal is to restore frequency without overloading system
  ERCOT to provide draft NOGRR language to provide Ops/Planning expectations
  Also Compliance Survey language to match expectations
Other discussion points
  At least two scenarios of different UFLS where event occurs during normal operations, versus EEA operations
  Request ERCOT provide Load Resource details in DSP footprint with survey (details in Appendix)
  How to consider equipped versus armed Load Resources
  Complexities with ERS- but much lower MW amount than Load Resources

## Slide 6: Goal for this workshop
Review Draft NOGRR
  Consider approach and the four areas of change proposed
    Removing this exclusion of Load Resources equipped with high-set underfrequency relays to preserve the expected system-wide 25% response in an underfrequency event,
    ERCOT to provide an inventory to the DSP of the registered Load Resources in the DSP footprint prior to each annual survey (details in Appendix),
    Retire Summer 2001 five year study reference to avoid any conflicts with current NERC PRC-006.
    Add clarification that in the case of a UFLS activation, DSP load relief would not include amounts of Load Resource and ERS already deployed prior to UFLS activation.
  Other issues to be addressed?

## Slide 7
APPENDIX:
NERC requirement excerpt
UFLS examples
Potential Load Resource data to provide

## Slide 8: Appendix- NERC Requirement
NERC standard PRC-006-2 — Automatic Underfrequency Load Shedding:
Requirement 9. Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. [VRF: High][Time Horizon: Long-term Planning]
Measurement 9. Each UFLS Entity shall have dated evidence such as spreadsheets summarizing feeder load armed with UFLS relays, spreadsheets with UFLS relay settings, or other dated documentation that it provided automatic tripping of load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, per Requirement R9.

## Slide 9: Example
Load 20MW
Load 20MW
Load 20MW
Load 20MW
Load 20MW
LR = 1MW
Current Annual Survey language could imply this methodology:
Actual System Load = 100 MW
#1
#2
#4
#3
#5
LR = 10MW
TDSP
X
X
Survey System Load = 100 – 40 (Feeders with any LR) = 60 MW
TDSP Breaker #1 armed at 59.3 = 20MW shed (20/60 = 33%)
TDSP Breaker #2 armed at 58.9 = 20MW shed (20/60 = 33%)
TDSP Breaker #3 armed at 58.5 = 20MW shed (20/60 = 33%)

## Slide 10: Example
Load 20MW
Load 20MW
Load 20MW
Load 20MW
Load 20MW
LR = 1MW
ERCOT assumption in Planning and Operations:
System Load at 60Hz = 100 MW
#1
#2
#4
#3
#5
LR = 10MW
TDSP
X
X
System Load in EEA3 or 59.7 = 100 – 11MW LR = 89 MW
TDSP Breaker #1 armed at 59.3 = 20MW shed (20/89 = 22%)
TDSP Breaker #2 armed at 58.9 = 20MW shed (20/89 = 22%)
TDSP Breaker #3 armed at 58.5 = 20MW shed (20/89 = 22%)
Load 19MW
----------------
Load 10MW
-----------------

## Slide 11: Potential Load Resource data to be provided
TDSP shown on Registration Form
  TDSP Duns
From the Load Resource Asset Registration Form
  Dispatch Asset Code
  ESIID (Load Resources for NOIEs will have a non-settlement ESIID)
  Station the Load Resource is mapped to in the Network Operations Model
  PTI Number
  Transmission Transformer Load Name
  Maximum Registered Interruptible Load
Historical Data (more analysis needed)
  Average hourly RRS Responsibility for LR during a predefined date range
  Maximum RRS Responsibility during the same time period