## Print Form
|  |  | Meter Compensation Calculations for: |  |  |  | ERCOT
|  |  |  | Date: | 2000-12-14
Transformer Information |  |  |  | Transmission Line Information |  |  | Meter Information
Xfmr Manufacturer |  | ABB |  | Line Type |  | 4/0 ACSR | PTR (xxx/1) | 60
Xfmr Serial Number |  | 1000001 |  | Line Length (miles) |  | 7.36 | CTR (xxx/1) | 120
Xfmr Size (KVA) |  | 12000 |  | Line Res.per mile @ 50 C |  | 0.592 | Meter Rated volt (v) | 120
Xfmr Pri. test volt (p-p-v) |  | 110000 |  | *Total Line Res. |  | 4.3571 | Meter Class amp (A) | 20
Xfmr Sec. test volt (p-p-v) |  | 13090 |  | *Line Loss (VA) |  | 266549.0817 | Number of elements | 3
Xfmr No-Load loss (Watts) |  | 22200 |  |  |  |  | *Meter Nominal Watts (watts) | 3600
Xfmr Excitation Current (%) |  | 0.45 |  |  |  |  | *Nominal CT Primary amp (A) | 1200
Xfmr Load loss (Watts) |  | 51360 |  |  |  |  | *Meter Secondary test volt (v) | 125.9586
Xfmr Impedance (%) |  | 8.84 |  |  |  |  | *Nominal Primary VA (VA) | 25920000
*Xfmr sec. test amp(A) |  | 529.2745
*Xfmr Pri Amp @ 1/2 Mtr Cl (A): |  | 142.8
Loss Constants | [6 empty] | Meter % Registration
*No Load VA loss (VA) |  | 54000 |  |  |  |  | FL Watt Reg. @ Unity PF (%)1 | 101.1789
*No Load loss ph angle(alpha) |  | 65.7253 |  |  |  |  | FL Watt Reg. @ 50% PF (%)1 | 102.3579
*No Load Var loss (Var) |  | 49225.6031 |  |  |  |  | LL Watt Reg. @ Unity PF (%)1 | 101.6571
*Load VA loss (VA) |  | 1060800 |  |  |  |  | FL Var Reg. @ ~ (%)1 | 110.8194
*Load loss ph angle(beta) |  | 87.2249 |  |  |  |  | LL Var Reg. @ ~ (%)1 | 104.1796
*Load Var loss (Var) |  | 1059555.9402 |  |  |  |  | 1Data from "Meter % Reg.-Data Entry" Sheet
% Transformer Losses |  |  |  | % Transmission Line Losses |  |  | % Total Losses
% Xfmr Watt Fe Loss |  | 0.077736 |  |  |  |  | %Tot. Watt Fe Loss | 0.077736
% Xfmr Watt Cu Loss |  | 1.0186 |  | % Line Watt Cu Loss |  | 1.0284 | %Tot. Watt Cu Loss | 2.0469
% Xfmr Var Fe Loss |  | 0.15645 |  |  |  |  | %Tot. Var Fe Loss | 0.15645
% Xfmr Var Cu Loss |  | 21.0131 |  |  |  |  | %Tot. Var Cu Loss | 21.0131
*Calculated values
Where: | Xfmr Sec. test amps=(Xfmr rating in VA)/(Xfmr secondary test p-p volt x Sqrt 3)
Xfmr Pri. Amp @ 1/2Mtr CL=(Xfmr Secondary test p-p volt/Xfmr Primary test p-p volt) x Nominal CT Primary Amp
Total Line Res.=Line Length x Line Res. (per mile)
Line Loss=3 x Total Line Res. x (Xfmr Primary Amp @ 1/2 Meter Class amp)^2
Meter Nominal Watts=(Meter Class amp/2) x Meter Rated voltage x Number of elements
Nominal CT Primary Amps=(Meter Class amp/2) x CTR
Meter secondary test Volt=(Xfmr sec test volt)/(PTR x Sqrt 3) for 3 elm; (Xfmr sec test volt)/(PTR) for 2 elm
Nominal Primary VA=CTR x PTR x Meter Nominal Watts
No Load VA loss=(Xfmr Excitation current x Xfmr rating in VA) / 100
No Load loss phase angle=acos(Xfmr No Load watts loss/No Load VA loss)
No Load Var Loss=No Load VA loss x sin(No Load loss phase angle (alpha))
Load VA loss=(Xfmr Impedance x Xfmr rating in VA ) / 100
Load loss ph angle (beta)=acos(Xfmr load loss/Load VA loss)
Load Var loss=Load VA loss x sin(Load loss phase angle (beta)
% Watt Fe Loss=((Xfmr No-load loss x (Meter rated volt/Meter sec. test volt)^2) / Nominal Primary VA) x 100
% Watt Cu Loss=((Xfmr Load loss x ((Meter Class amp/2) x (CTR/Xfmr sec. test amp))^2) / Nominal Primary VA) x 100
% Var Fe Loss=((No Load Var loss x (Meter Rated volt/Meter Sec. test volt)^4) / Nominal Primary VA) x 100
% Var Cu Loss=((Load Var loss x ((Meter Class amp/2) x (CTR/Xfmr sec. test amp))^2) / Nominal Primary VA) x 100
% Line Cu Loss=(Line Loss VA/ Nominal Primary VA) x 100
% Total Losses= %Xfmr(Fe or Cu) losses + %Line(Fe or Cu) losses

## Xfmr & Line Loss-Data Entry
Data Entry Form
Enter Data in Yellow areas only
Calculated values are in blue areas
|  |  |  | Site Name: | ERCOT
|  |  |  | Date: | 2000-12-14
| Transfomer Information |  |  |  | Transmission line information |  |  |  | Meter Information
| Transformer Manufacturer | ABB |  |  | Line Type: | 4/0 ACSR |  | PT ratio (xxx:1): | 60
| Transformer Serial Number | 1000001 |  |  | Line Length: | 7.36 |  | CT ratio (xxx:1): | 120
| Transformer Size (KVA): | 12000 |  |  | Line Res.: | 0.592 |  | Meter Rated Voltage: | 120
| Xfmr Primary test Voltage (pvolt-pvolt): | 110000 |  |  | *Total Line Res.: | 4.3571 |  | Meter Class Amps: | 20
| Xfmr Secondary test Voltage (pvolt-pvolt): | 13090 |  |  | *Line Loss (VA): | 266549.0817 |  | Meter Number of Elements (2 or3): | 3
| Xfmr No Load Loss (watts): | 22200 | [5 empty] | *Meter Nominal Watts (watts): | 3600
| Xfmr Excitation Current(%): | 0.45 | [5 empty] | *Nominal CT Primary Amps (a) : | 1200
| Xfmr Load Loss (watts): | 51360 | [5 empty] | *Meter Secondary test Voltage (v): | 125.9586
| Xfmr Impedence (%): | 8.84 | [5 empty] | *Nominal Primary VA (va): | 25920000
| *Xfmr sec. amps @ Xfmr sec. test volt(A): | 529.2745
| *Xfmr Pri Amps @ 1/2 Mtr Cl (A): | 142.8
Loss Constants
| *No load VA Loss (VA): | 54000
| *No Load loss phase angle (alpha) | 65.7253
| *No Load Var loss (Var): | 49225.6031
| *Load VA Loss (VA): | 1060800
| *Load loss phase angle (beta) | 87.2249
| *Load Var loss (Var): | 1059555.9402
*Xfmr losses: |  |  |  | *Line losses: |  |  | *Total losses:
% Watt Iron Loss (%): |  | 0.077736 | [5 empty] | % Watt Iron Losses(%) | 0.077736
% Watt Cu Loss (%): |  | 1.0186 |  |  | % Watt Line Cu Loss (%) | 1.0284 |  | % Watt Cu Losses(%) | 2.0469
% Var Iron Loss (%): |  | 0.15645 | [5 empty] | % Var Iron Losses(%) | 0.15645
% Var Cu Loss (%): |  | 21.0131 | [5 empty] | % Var Cu Losses(%) | 21.0131

## Meter % Registration-Data Entry
Percent Registration & Error Calculations for Meters with Transformer and Line Loss
Meter Test Set Settings
Data Entry
|  | Applied Meter Voltage (AV) = | 120 | volts
|  | Applied Meter Full Load Current (AI) = | 5 | amps
|  | Applied Meter Light Load Current (AI) = | 0.5 | amps
|  | Applied Phase angle for Var test (~) = | 90 | degrees
|  | Meter Rated Voltage (MRV) = | 120 | volts
|  | Meter Class Amps (MCA) = | 20 | amps
* Transformer & Line Loss Data
|  | * % Watt Iron (Fe) Loss = | 0.077736 | %
|  | * % Watt Copper (Cu) Loss = | 2.0469 | %
|  | * % Var Iron (Fe) Loss = | 0.15645 | %
|  | * % var Copper (Cu) Loss = | 21.0131 | %
|  | *Full Load Percent Registration & Error Results |  |  | *Light Load Percent Registration & Error Results
|  | % Watt |  |  | % Watt
|  | * % TLC Watt Registration @ Unity PF = | 101.1789 | % | * % TLC Watt Registration @ Unity PF = | 101.6571 | %
|  | * % TLC Watt Error @ Unity PF = | 1.1789 | % | * % TLC Watt Error @ Unity PF = | 1.6571 | %
|  | * % TLC Watt Registration @ 50% PF = | 102.3579 | %
|  | * % TLC Watt Error @ 50% PF = | 2.3579 | %
|  | %Var |  |  | %Var
|  | * % TLC Var Registration @ (~) = | 110.8194 | % | * % TLC Var Registration @ (~) = | 104.1796 | %
|  | * % TLC Var Error @ (~) = | 10.8194 | % | * % TLC Var Error @ (~) = | 4.1796 | %
* Calculations for Watt and Var Percent Registration & Error
Where:
% Watt Iron (Fe) Loss = Data From Transformer and Line Loss Compensation Calculation Sheet
% Watt Copper (Cu) Loss = Data From Transformer and Line Loss Compensation Calculation Sheet
% Var Iron (Fe) Loss = Data From Transformer and Line Loss Compensation Calculation Sheet
% Var Copper (Cu) Loss = Data From Transformer and Line Loss Compensation Calculation Sheet
% TLC Watt Registration @ Unity PF=1/Cos(0) x [(MCA/2 / AI) x (AV / MRV) x %Watt Fe Loss] + [(AI / MCA/2) x (MRV / AV) x % Watt Cu Loss]+100
% TLC Watt Error @ Unity PF=1/Cos(0) x [(MCA/2 / AI) x (AV / MRV) x %Watt Fe Loss] + [(AI / MCA/2) x (MRV / AV) x % Watt Cu Loss]
% TLC Watt Registration @ 50% PF=1/Cos(60) x [(MCA/2 / AI) x (AV / MRV) x %Watt Fe Loss] + [(AI / MCA/2) x (MRV / AV) x % Watt Cu Loss]+100
% TLC Watt Error @ 50% PF =1/Cos(60) x [(MCA/2 / AI) x (AV / MRV) x %Watt Fe Loss] + [(AI / MCA/2) x (MRV / AV) x % Watt Cu Loss]
% TLC Var Registration @ (~) =1/Sin(~) x [(MCA/2 / AI) x (AV^3 / MRV^3) x %Var Fe Loss] + [(AI / MCA/2) x (MRV / AV) x % Var Cu Loss]+100
% TLC Var Error @ (~) =1/Sin(~) x [(MCA/2 / AI) x (AV^3 / MRV^3) x %Var Fe Loss] + [(AI / MCA/2) x (MRV / AV) x % Var Cu Loss]