## Summary
Release Date: May 2, 2017
Preliminary
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Fall 2017
SUMMARY
The ERCOT Region is expected to have sufficient installed generating capacity to serve forecasted peak demands in the upcoming fall season (October- November 2017).
The peak load forecast used for this SARA report is 56,097 MW. Total generation resource capacity of 86,806 MW currently is expected to be available for peak load hours in the upcoming fall. This total includes planned capacity additions of 3,862 MW, consisting of 2,875 MW fueled by natural gas, 654 MW of wind and 333 MW of grid-scale solar. Installed capacities for wind and solar are 1,762 MW and 529 MW, respectively. The wind capacity values included in the report reflect a capacity contribution of 35% for non-coastal resources and 44% for coastal resources. The solar summer peak-hour capacity values reflect a capacity contribution of 63%.
This preliminary fall SARA report includes a unit outage forecast of 14,272 MW developed from outage data for the most recent five historical fall seasons along with recent updates to generating capacity ratings.
At this time, ERCOT has not received information from generation resource owners indicating plans to mothball or retire available generation capacity for the fall season.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Fall 2017 - Preliminary
Release Date: May 2, 2017
Forecasted Capacity and Demand
|  | Operational Resources (thermal and hydro), MW | 68653.3 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
|  | Switchable Capacity Total, MW | 3911.8 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
|  | less Switchable Capacity Unavailable to ERCOT, MW | -843.8 | Based on survey responses of Switchable Resource owners
|  | Mothball Resources, MW | 0 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
|  | Private Use Network Capacity Contribution, MW | 3752.31 | Average capability of the top 20 hours in the summer peak seasons for the past three years (2014-2016)
|  | Non-Coastal Wind Resources Capacity Contribution, MW | 5868.975 | Based on 35% of installed capacity for non-coastal wind resources per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Coastal Wind Resources Capacity Contribution, MW | 942.744 | Based on 44% of installed capacity for coastal wind resources per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Solar Utility-Scale, Peak Average Capacity Contribution, MW | 493.542 | Based on 63% of rated capacity for solar resources per Nodal Protocols Section 3.2.6.2.2
|  | RMR Resources to be under Contract, MW | 0
|  | Non-Synchronous Ties Capacity Contribution, MW | 165.8 | Average capability of the top 20 hours in the summer peak seasons for the past three years (2014-2016)
|  | Planned Thermal Resources with Signed IA, Air Permits and Water Rights, MW | 2875 | Based on in-service dates provided by developers of generation resources
|  | Planned Non-Coastal Wind with signed IA , MW | 472.675 | Based on in-service dates provided by developers of generation resources and 35% of installed capacity for non-coastal wind resources
|  | Planned Coastal Wind with signed IA , MW | 180.84 | Based on in-service dates provided by developers of generation resources and 44% of installed capacity for coastal wind resources
|  | Planned Solar Utility-Scale with signed IA, MW | 333.27 | Based on 63% of rated capacity for solar resources per Nodal Protocols Section 3.2.6.2.2
| [a] Total Resources, MW |  | 86806.456
| [b] Peak Demand, MW |  | 56097 | Based on average peak weather conditions for the past 13 years (2002 – 2015)
| [c] Reserve Capacity [a - b], MW |  | 30709.456
Range of Potential Risks
|  |  | Forecasted Season Peak Load | Forecasted Season Peak Load / Extreme Generation Outages | Extreme Peak Load / Typical Generation Outages
|  | Seasonal Load Adjustment | 0 | 3814 | 3814 | Based on fall 2014 weather
|  | Typical Maintenance Outages | 10616 | 10616 | 10616 | Based on historical average of planned outages for October through November weekdays (starting in April 2012), and accounts for recent capacity rating changes for operational units
|  | Typical Forced Outages, Thermal | 3656 | 3656 | 3656 | Based on historical average of planned outages for October through November weekdays (starting in April 2012), and accounts for recent capacity rating changes for operational units
|  | 90th Percentile Forced Outages, Thermal | 0 | 0 | 2090 | Based on historical forced outages assuming a 90% confidence interval
| [d] Total Uses of Reserve Capacity |  | 14272 | 18086 | 20176
| [e] Capacity Available for Operating Reserves (c-d), MW |  | 16437.456 | 12623.456 | 10533.456
Less than 2,300 MW indicates risk of EEA1

## Fall_Capacities
Unit Capacities - Fall
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | START YEAR | CAPACITY (MW)
3 | Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1222
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1209
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1318
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1325
8 | BIG BROWN U1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 606
9 | BIG BROWN U2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 602
10 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 660
11 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 603
12 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 603
13 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 444
14 | GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470
15 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
16 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775
17 | J T DEELY U1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 420
18 | J T DEELY U2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420
19 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831
20 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858
21 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 815
22 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
23 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
24 | MONTICELLO U1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 572
25 | MONTICELLO U2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 572
26 | MONTICELLO U3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795
27 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840
28 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825
29 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
30 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
31 | SANDOW U5 |  | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 600
32 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970
33 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 158
34 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 158
35 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 659
36 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 658
37 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577
38 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610
39 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 149
40 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 149
41 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 160
42 | BARNEY M DAVIS REPOWER CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 161
43 | BARNEY M DAVIS REPOWER CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 161
44 | BARNEY M DAVIS REPOWER STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 322
45 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 157
46 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 157
47 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 236
48 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 160.5
49 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 83.3
50 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 160.5
51 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 159.5
52 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 221.5
53 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 168
54 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 168
55 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270
56 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 77
57 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 77
58 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 71
59 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 168
60 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 168
61 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 182
62 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 74
63 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 67
64 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 100
65 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 73
66 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 68
67 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 105
68 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 171
69 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 164
70 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 164
71 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 146
72 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 194
73 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 206
74 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 194
75 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 206
76 | DEER PARK ENERGY CENTER STG |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290
77 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 179
78 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 231
79 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 127
80 | FERGUSON REPLACEMENT CTG1 |  | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 173
81 | FERGUSON REPLACEMENT CTG2 |  | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 173
82 | FERGUSON REPLACEMENT STG |  | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 186
83 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 178
84 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 170
85 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 170
86 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 178
87 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 170
88 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 170
89 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 420
90 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 420
91 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 155.2
92 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 155.2
93 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 177.6
94 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 155.4
95 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 155.4
96 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 176.5
97 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 158
98 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 158
99 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 158
100 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 158
101 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 200
102 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 200
103 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 220
104 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 220
105 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 225
106 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 225
107 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 145
108 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 145
109 | HIDALGO ENERGY CENTER STG |  | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 173
110 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 150
111 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 150
112 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 285
113 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 150
114 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 150
115 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 285
116 | JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163
117 | JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
118 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 171
119 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 161
120 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 161
121 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 166
122 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
123 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
124 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 178
125 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 172
126 | LOST PINES POWER STG |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 188
127 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 212.5
128 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 212.5
129 | MAGIC VALLEY STATION STG |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 254.9
130 | MIDLOTHIAN ENERGY FACILITY CS 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 235
131 | MIDLOTHIAN ENERGY FACILITY CS 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 235
132 | MIDLOTHIAN ENERGY FACILITY CS 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 235
133 | MIDLOTHIAN ENERGY FACILITY CS 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 235
134 | MIDLOTHIAN ENERGY FACILITY CS 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 252
135 | MIDLOTHIAN ENERGY FACILITY CS 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 252
136 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 161
137 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 161
138 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 322
139 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 155.8
140 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 149.5
141 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 152
142 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 150.3
143 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 207.7
144 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 207.7
145 | PANDA SHERMAN POWER CTG1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 218.5
146 | PANDA SHERMAN POWER CTG2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 218.5
147 | PANDA SHERMAN POWER STG |  | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 353.1
148 | PANDA TEMPLE I POWER CTG1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 218.5
149 | PANDA TEMPLE I POWER CTG2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 218.5
150 | PANDA TEMPLE I POWER STG |  | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 353.1
151 | PANDA TEMPLE II POWER CTG1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 218.5
152 | PANDA TEMPLE II POWER CTG2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 218.5
153 | PANDA TEMPLE II POWER STG |  | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 353.1
154 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 86
155 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 86
156 | PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87
157 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 168
158 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 168
159 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 168
160 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 81
161 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 81
162 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
163 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 80
164 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 80
165 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
166 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 162
167 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 162
168 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 162
169 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323
170 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
171 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 51
172 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
173 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
174 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 161
175 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 150
176 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 20
177 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 38
178 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57
179 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57
180 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57
181 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57
182 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104
183 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57
184 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57
185 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57
186 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57
187 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104
188 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 99.1
189 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 99.1
190 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 99.1
191 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.5
192 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 171
193 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 132
194 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20
195 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20
196 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20
197 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17
198 | WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 275
199 | WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 275
200 | WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 290
201 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 227
202 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 227
203 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 286
204 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 19
205 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 46.5
206 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 48.5
207 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 49
208 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 49
209 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 49
210 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 49
211 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 74
212 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 73
213 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 72
214 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 71
215 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 153.6
216 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 153.6
217 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 42
218 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 42
219 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 42
220 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 42
221 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 57
222 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 57
223 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 57
224 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 50
225 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 57
226 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 57
227 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.2
228 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.2
229 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.2
230 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 93
231 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 90.2
232 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 45
233 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46
234 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 44
235 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46
236 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 77
237 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 77
238 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 77
239 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 77
240 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 77
241 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 77
242 | PEARSALL IC ENGINE PLANT A |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
243 | PEARSALL IC ENGINE PLANT B |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
244 | PEARSALL IC ENGINE PLANT C |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
245 | PEARSALL IC ENGINE PLANT D |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
246 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 71
247 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 70
248 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 73
249 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 74
250 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 74
251 | REDGATE A |  | REDGATE_AGR_A | HIDALGO | GAS | SOUTH | 2016 | 56.3
252 | REDGATE B |  | REDGATE_AGR_B | HIDALGO | GAS | SOUTH | 2016 | 56.3
253 | REDGATE C |  | REDGATE_AGR_C | HIDALGO | GAS | SOUTH | 2016 | 56.3
254 | REDGATE D |  | REDGATE_AGR_D | HIDALGO | GAS | SOUTH | 2016 | 56.3
255 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 1994 | 104
256 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 1994 | 104
257 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75
258 | SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 13.5
259 | SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 13.5
260 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81
261 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81
262 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47
263 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47
264 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47
265 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47
266 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47
267 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47
268 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46
269 | SKY GLOBAL POWER ONE A |  | SKY1_SKY1A | COLORADO | GAS | SOUTH | 2016 | 26.7
270 | SKY GLOBAL POWER ONE B |  | SKY1_SKY1B | COLORADO | GAS | SOUTH | 2016 | 26.7
271 | T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57
272 | T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57
273 | T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57
274 | T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57
275 | T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57
276 | T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57
277 | T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
278 | TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 89
279 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
280 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
281 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
282 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47
283 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13
284 | W A PARISH - PETRA NOVA CTG |  | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 83
285 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44
286 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44
287 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44
288 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44
289 | B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 330
290 | CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
291 | CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
292 | DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 108.5
293 | DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 320
294 | DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 420
295 | GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234
296 | GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
297 | HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
298 | HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
299 | HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
300 | LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
301 | LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523
302 | MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122
303 | MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118
304 | MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568
305 | O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
306 | O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410
307 | PEARSALL STG U1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 20
308 | PEARSALL STG U2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 23
309 | PEARSALL STG U3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 21
310 | POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 20
311 | POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 24
312 | POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41
313 | R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 1968 | 75
314 | R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 1972 | 120
315 | R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 1975 | 208
316 | RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
317 | RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
318 | RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
319 | SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
320 | SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135
321 | SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 336
322 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 57
323 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
324 | STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
325 | STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
326 | TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235
327 | V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220
328 | V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
329 | V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
330 | W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169
331 | W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169
332 | W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 246
333 | W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 536
334 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
335 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
336 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
337 | FORT WORTH METHANE LFG |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6
338 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
339 | MCKINNEY LFG |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2
340 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2
341 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
342 | TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2
343 | VIRIDIS ENERGY-ALVIN LFG |  | DG_AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7
344 | VIRIDIS ENERGY-HUMBLE LFG |  | DG_HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10
345 | VIRIDIS ENERGY-LIBERTY LFG |  | DG_LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9
346 | VIRIDIS ENERGY-TRINITY BAY LFG |  | DG_TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9
347 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
348 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
349 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
350 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
351 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
352 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2012 | 0
353 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 68249.6
354
355 | Operational Resources (Hydro)
356 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
357 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
358 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
359 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
360 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
361 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
362 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
363 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
364 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
365 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
366 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
367 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
368 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
369 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
370 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
371 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
372 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
373 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
374 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
375 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29
376 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 24
377 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 24
378 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.4
379 | EAGLE PASS HYDRO |  | DG_EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
380 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | DG_CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
381 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
382 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
383 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
384 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
385 | Operational Capacity Total (Hydro) | [6 empty] | 555.1
386 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 403.7
387
388 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | 0
389 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 68653.3
390
391 | Operational Resources (Switchable)
392 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS | WEST | 2016 | 54.6
393 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS | WEST | 2016 | 54.6
394 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS | WEST | 2016 | 54.6
395 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS | WEST | 2016 | 190
396 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 190
397 | ELK STATION CTG 3 |  | AEEC_ELK_3 | HALE | GAS | WEST | 2016 | 190
398 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 178
399 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 180
400 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 307
401 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 178
402 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 180
403 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 307
404 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 180
405 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 180
406 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 180
407 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400
408 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 162
409 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 179
410 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 178
411 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 389
412 | Switchable Capacity Total | [6 empty] | 3911.8
413
414 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  | GAS |  |  | -843.8
415
416 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | COAL |  |  | 0
417
418 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 3516
419 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  | PUN_CAP_ADJUST |  | GAS |  |  | 236.31
420
421 | Operational Resources (Wind)
422 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8
423 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND | NORTH | 2007 | 120
424 | BLUE SUMMIT WIND 5 |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9
425 | BLUE SUMMIT WIND 6 |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4
426 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND | WEST | 2012 | 150
427 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND | PANHANDLE | 2015 | 149.8
428 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6
429 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5
430 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117
431 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2
432 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88
433 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90
434 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114
435 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5
436 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120
437 | CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5
438 | CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186
439 | CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5
440 | CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | COKE | WIND | WEST | 2008 | 112.5
441 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75
442 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75
443 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND | WEST | 2008 | 126.5
444 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND | PANHANDLE | 2017 | 50
445 | DESERT SKY WIND 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84
446 | DESERT SKY WIND 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5
447 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND | PANHANDLE | 2016 | 100.2
448 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND | PANHANDLE | 2016 | 100.2
449 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7
450 | ELECTRA WIND 1 |  | ELECTRAW_UNIT1 | WILBARGER | WIND | WEST | 2017 | 98.9
451 | ELECTRA WIND 2 |  | ELECTRAW_UNIT2 | WILBARGER | WIND | WEST | 2017 | 131.1
452 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2
453 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80
454 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6
455 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6
456 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 107.4
457 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND | PANHANDLE | 2014 | 103.8
458 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND | WEST | 2003 | 99
459 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND | WEST | 2003 | 61
460 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND | WEST | 2015 | 150
461 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND | WEST | 2016 | 150
462 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND | WEST | 2016 | 119.9
463 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5
464 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND | PANHANDLE | 2015 | 99.9
465 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND | PANHANDLE | 2015 | 100
466 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND | SOUTH | 2016 | 50
467 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND | SOUTH | 2016 | 100
468 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND | SOUTH | 2016 | 100
469 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND | WEST | 2017 | 131.1
470 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND | WEST | 2017 | 98.9
471 | HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6
472 | HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 158
473 | HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 223.5
474 | HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 115
475 | INADALE WIND |  | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6
476 | INDIAN MESA WIND |  | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5
477 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND | SOUTH | 2015 | 19.7
478 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND | SOUTH | 2015 | 230
479 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND | SOUTH | 2017 | 96
480 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND | SOUTH | 2017 | 74
481 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND | SOUTH | 2017 | 30
482 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND | PANHANDLE | 2015 | 146.2
483 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND | PANHANDLE | 2015 | 153.6
484 | KEECHI WIND 138 KV JOPLIN |  | KEECHI_U1 | JACK | WIND | NORTH | 2015 | 110
485 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3
486 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3
487 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3
488 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3
489 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155
490 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND | NORTH | 2015 | 103.8
491 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND | NORTH | 2015 | 106.3
492 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200
493 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100
494 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100
495 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND | PANHANDLE | 2015 | 100
496 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND | PANHANDLE | 2015 | 100
497 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5
498 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51
499 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5
500 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24
501 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND | SOUTH | 2015 | 200
502 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND | SOUTH | 2016 | 200
503 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND | SOUTH | 2016 | 110
504 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND | WEST | 2017 | 115.2
505 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND | WEST | 2017 | 115.2
506 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND | WEST | 2015 | 105.6
507 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND | WEST | 2015 | 105.6
508 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND | PANHANDLE | 2014 | 144.3
509 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND | PANHANDLE | 2014 | 144.3
510 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND | PANHANDLE | 2008 | 150
511 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND | WEST | 2009 | 92.6
512 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND | WEST | 2009 | 60
513 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8
514 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND | PANHANDLE | 2017 | 150
515 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2
516 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2
517 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 94.2
518 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 96.6
519 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5
520 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5
521 | PANTHER CREEK WIND 3 |  | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5
522 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5
523 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2
524 | PYRON WIND |  | PYR_PYRON1 | SCURRY | WIND | WEST | 2008 | 249
525 | RATTLESNAKE DEN WIND PHASE 1 G1 |  | RSNAKE_G1 | GLASSCOCK | WIND | WEST | 2015 | 104.3
526 | RATTLESNAKE DEN WIND PHASE 1 G2 |  | RSNAKE_G2 | GLASSCOCK | WIND | WEST | 2015 | 103
527 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84
528 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209
529 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND | PANHANDLE | 2015 | 150
530 | SAND BLUFF WIND |  | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90
531 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND | SOUTH | 2015 | 76
532 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND | NORTH | 2012 | 150
533 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND | WEST | 2015 | 204.1
534 | SHERBINO 1 WIND |  | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150
535 | SHERBINO 2 WIND |  | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 145
536 | SILVER STAR WIND |  | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60
537 | SNYDER WIND |  | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63
538 | SOUTH PLAINS WIND I |  | SPLAIN1_WIND1 | FLOYD | WIND | PANHANDLE | 2015 | 102
539 | SOUTH PLAINS WIND 2 |  | SPLAIN1_WIND2 | FLOYD | WIND | PANHANDLE | 2015 | 98
540 | SOUTH PLAINS WIND II A |  | SPLAIN2_WIND21 | FLOYD | WIND | PANHANDLE | 2016 | 148.5
541 | SOUTH PLAINS WIND II B |  | SPLAIN2_WIND22 | FLOYD | WIND | PANHANDLE | 2016 | 151.8
542 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND | WEST | 2008 | 98.2
543 | SPINNING SPUR WIND TWO |  | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161
544 | SPINNING SPUR 3 [WIND 1] |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND | PANHANDLE | 2015 | 96
545 | SPINNING SPUR 3 [WIND 2] |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND | PANHANDLE | 2015 | 98
546 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120
547 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND | WEST | 2014 | 211.2
548 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND | WEST | 2015 | 164.7
549 | SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.6
550 | SWEETWATER WIND 2A |  | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 18.1
551 | SWEETWATER WIND 2B |  | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 105
552 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5
553 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5
554 | SWEETWATER WIND 4-5 |  | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.2
555 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.7
556 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8
557 | TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7
558 | TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6
559 | TRENT WIND |  | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150
560 | TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | YOUNG | WIND | WEST | 2012 | 117.5
561 | TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | YOUNG | WIND | WEST | 2012 | 107.5
562 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5
563 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND | NORTH | 2017 | 125.6
564 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND | PANHANDLE | 2016 | 114.9
565 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND | PANHANDLE | 2016 | 142.3
566 | WEST TEXAS WIND |  | SW_MESA_SW_MESA | UPTON | WIND | WEST | 1999 | 80.3
567 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND | PANHANDLE | 2007 | 57
568 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND | SOUTH | 2012 | 91
569 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND | WEST | 2014 | 67.6
570 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND | WEST | 2012 | 30
571 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5
572 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2
573 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND | PANHANDLE | 2007 | 1
574 | Operational Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 16768.5
575 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PEAK_PCT_NC | % |  |  |  | 35
576
577 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100
578 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102
579 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165
580 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
581 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
582 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
583 | LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6
584 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
585 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
586 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
587 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
588 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
589 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
590 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
591 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2017 | 95.2
592 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
593 | Operational Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 2142.6
594 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 44
595
596 | Operational Wind Capacity Total (All Counties) |  | WIND_OPERATIONAL |  |  |  |  | 18911.1
597
598 | Operational Resources (Solar)
599 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
600 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 121.1
601 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2014 | 22
602 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
603 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
604 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 95
605 | OCI ALAMO 6 (WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2017 | 108.3
606 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
607 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
608 | BLUE WING 2 SOLAR |  | DG_ELEM_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
609 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
610 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
611 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 104.5
612 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.8
613 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.8
614 | BECK 1 |  | DG_CECSOLAR_DG_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1
615 | FIFTH GENERATION SOLAR 1 |  | DG_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 1.6
616 | HM SEALY SOLAR 1 |  | DG_SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6
617 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CCS1 | DENTON | SOLAR | NORTH | 2015 | 2
618 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
619 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
620 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
621 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
622 | Operational Capacity Total (Solar) | [6 empty] | 783.4
623 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 63
624
625 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0
626
627 | Non-Synchronous Tie Resources
628 | EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600
629 | NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220
630 | EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30
631 | LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100
632 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150
633 | SHARYLAND RAILROAD TIE 2 |  | DC_R2 | HIDALGO |  | SOUTH |  | 150
634 | Non-Synchronous Ties Total | [6 empty] | 1250
635 | Non-Synchronous Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 165.8
636
637 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Water Rights
638 | BLUE SUMMIT BATTERY | 16INR0122 |  | WILBARGER | WIND | WEST | 2017 | 0
639 | COLORADO BEND II | 17INR0007 |  | WHARTON | GAS | SOUTH | 2017 | 1148
640 | TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2019 | 0
641 | FGE TEXAS I PROJECT | 16INR0010 |  | MITCHELL | GAS | WEST | 2019 | 0
642 | PHR PEAKERS [BAC_CTG1-6] | 14INR0038 |  | GALVESTON | GAS | HOUSTON | 2017 | 390
643 | INDECK WHARTON ENERGY CENTER | 15INR0023 |  | WHARTON | GAS | SOUTH | 2019 | 0
644 | PINECREST ENERGY CENTER PROJECT | 16INR0006 |  | ANGELINA | GAS | NORTH | 2020 | 0
645 | WOLF HOLLOW 2 | 17INR0009 |  | HOOD | GAS | NORTH | 2017 | 1118
646 | FRIENDSWOOD G | 13INR0049 |  | HARRIS | GAS | HOUSTON | 2017 | 119
647 | BETHEL CAES PROJECT | 15INR0013 |  | ANDERSON | GAS | NORTH | 2020 | 0
648 | HALYARD HENDERSON | 16INR0045 |  | HENDERSON | GAS | NORTH | 2018 | 0
649 | HALYARD WHARTON ENERGY CENTER | 16INR0044 |  | WHARTON | GAS | SOUTH | 2018 | 0
650 | CASTLEMAN CHAMON | 17INR0042 |  | HARRIS | GAS | HOUSTON | 2017 | 100
651 | NASA-JSC CHP | 16INR0054 |  | HARRIS | GAS | HOUSTON | 2017 | 0
652 | FREEPORT LNG | 16INR0003 |  | BRAZORIA | GAS | COASTAL | 2018 | 0
653 | Planned Capacity Total (Coal, Gas & Storage) | [6 empty] | 2875
654
655 | Planned Wind Resources with Executed SGIA
656 | MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | COASTAL | 2017 | 161
657 | LONGHORN WIND SOUTH | 14INR0023b |  | BRISCOE | WIND | PANHANDLE | 2017 | 0
658 | MARIAH WIND A | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2018 | 0
659 | MARIAH DEL SUR | 13INR0010c |  | PARMER | WIND | PANHANDLE | 2018 | 0
660 | RATTLESNAKE DEN WIND 2 | 13INR0020b |  | GLASSCOCK | WIND | WEST | 2020 | 0
661 | PATRIOT WIND (PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2018 | 0
662 | COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2018 | 0
663 | PAMPA WIND | 12INR0018 |  | GRAY | WIND | PANHANDLE | 2018 | 0
664 | GRANDVIEW WIND 3 (CONWAY) | 13INR0005c |  | CARSON | WIND | PANHANDLE | 2017 | 0
665 | SCANDIA WIND DEF | 13INR0010def |  | PARMER | WIND | PANHANDLE | 2018 | 0
666 | PULLMAN ROAD WIND | 15INR0079 |  | RANDALL | WIND | PANHANDLE | 2018 | 0
667 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2017 | 0
668 | SALT FORK WIND | 14INR0062 |  | GRAY | WIND | PANHANDLE | 2017 | 174
669 | PALO DURO WIND | 15INR0050 |  | DEAF SMITH | WIND | PANHANDLE | 2018 | 0
670 | CAPROCK WIND | 10INR0009 |  | CASTRO | WIND | PANHANDLE | 2018 | 0
671 | TORRECILLAS WIND A | 14INR0045a |  | WEBB | WIND | SOUTH | 2017 | 0
672 | TORRECILLAS WIND B | 14INR0045b |  | WEBB | WIND | SOUTH | 2017 | 0
673 | CHANGING WINDS | 13INR0045 |  | CASTRO | WIND | PANHANDLE | 2018 | 0
674 | LOCKETT WIND FARM | 16INR0062b |  | WILBARGER | WIND | WEST | 2017 | 184
675 | WILLOW SPRINGS WIND | 14INR0060b |  | HASKELL | WIND | WEST | 2017 | 230
676 | FALVEZ ASTRA W | 15INR0074 |  | DEAF SMITH | WIND | PANHANDLE | 2017 | 163.2
677 | CHAPMAN RANCH WIND I | 16INR0055 |  | NUECES | WIND-C | COASTAL | 2017 | 250
678 | PUMPKIN FARM WIND | 16INR0037c |  | FLOYD | WIND | PANHANDLE | 2019 | 0
679 | ROCK SPRINGS VAL VERDE WIND | 11INR0082a |  | VAL VERDE | WIND | WEST | 2017 | 149.3
680 | MAGIC VALLEY WIND II (REDFISH 2A and 2B) | 14INR0041a |  | WILLACY | WIND-C | COASTAL | 2017 | 0
681 | SANTA RITA WIND | 16INR0091 |  | REAGAN | WIND | WEST | 2017 | 0
682 | SWISHER WIND | 13INR0038 |  | SWISHER | WIND | PANHANDLE | 2017 | 0
683 | BUCKTHORN WIND 1 | 14INR0057 |  | ERATH | WIND | NORTH | 2017 | 0
684 | FLUVANNA RENEWABLE 1 | 13INR0056 |  | SCURRY | WIND | WEST | 2017 | 0
685 | RTS WIND | 16INR0087 |  | MCCULLOCH | WIND | SOUTH | 2018 | 0
686 | SILVER CANYON WIND A | 12INR0002a |  | BRISCOE | WIND | PANHANDLE | 2017 | 0
687 | LOGAN'S GAP WIND II | 15INR0082 |  | COMANCHE | WIND | NORTH | 2017 | 0
688 | CANADIAN BREAKS WIND | 13INR0026 |  | OLDHAM | WIND | PANHANDLE | 2018 | 0
689 | SALT FORK WIND EXPANSION | 16INR0121 |  | CARSON | WIND | PANHANDLE | 2017 | 0
690 | CHOCOLATE BAYOU | 16INR0074 |  | BRAZORIA | WIND-C | COASTAL | 2018 | 0
691 | GOODNIGHT WIND | 14INR0033 |  | ARMSTRONG | WIND | PANHANDLE | 2018 | 0
692 | DERMOTT WIND 1 | 17INR0027 |  | SCURRY | WIND | WEST | 2017 | 253
693 | COYOTE WIND | 17INR0027b |  | SCURRY | WIND | WEST | 2018 | 0
694 | BEARKAT WIND A | 15INR0064 |  | GLASSCOCK | WIND | WEST | 2017 | 197
695 | BEARKAT WIND B | 15INR0064b |  | GLASSCOCK | WIND | WEST | 2018 | 0
696 | INFINITY LIVE OAK WIND | 12INR0060 |  | SCHLEICHER | WIND | WEST | 2017 | 0
697 | CACTUS FLATS WIND | 16INR0086 |  | CONCHO | WIND | WEST | 2018 | 0
698 | Planned Capacity Total (Wind) | [6 empty] | 1761.5
699
700 | Planned Wind Capacity Sub-total (Non-Coastal Counties) |  | WIND_PLANNED_NC |  |  |  |  | 1350.5
701 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PL_PEAK_PCT_NC | % |  |  |  | 35
702
703 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 411
704 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 44
705
706 | Planned Solar Resources with Executed SGIA
707 | FS BARILLA SOLAR 1B [HOVEY_UNIT2] | 12INR0059b |  | PECOS | SOLAR | WEST | 2017 | 7.4
708 | OCI ALAMO 6 (WEST TEXAS PHASE II) | 15INR0070_1b |  | PECOS | SOLAR | WEST | 2017 | 49
709 | SE BUCKTHORN WESTEX SOLAR (RIGGINS SOLAR) | 15INR0045 |  | PECOS | SOLAR | WEST | 2017 | 0
710 | LC NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2017 | 201
711 | PECOS SOLAR POWER I | 15INR0059 |  | PECOS | SOLAR | WEST | 2019 | 0
712 | BNB LAMESA SOLAR | 16INR0023 |  | DAWSON | SOLAR | WEST | 2017 | 101.6
713 | BNB LAMESA SOLAR B | 16INR0023b |  | DAWSON | SOLAR | WEST | 2018 | 0
714 | CAPRICORN RIDGE SOLAR | 16INR0019 |  | COKE | SOLAR | WEST | 2017 | 0
715 | UPCO POWER 1 (SP-TX-12) | 16INR0065 |  | UPTON | SOLAR | WEST | 2019 | 0
716 | CASTLE GAP SOLAR 2 | 16INR0065a |  | UPTON | SOLAR | WEST | 2020 | 0
717 | SP-TX-12-PHASE B | 16INR0065b |  | UPTON | SOLAR | WEST | 2017 | 120
718 | SOLAIREHOLMAN 1 | 15INR0061 |  | BREWSTER | SOLAR | WEST | 2017 | 50
719 | RE MAPLEWOOD 2A SOLAR | 17INR0020a |  | PECOS | SOLAR | WEST | 2018 | 0
720 | RE MAPLEWOOD 2B SOLAR | 17INR0020b |  | PECOS | SOLAR | WEST | 2019 | 0
721 | RE MAPLEWOOD 2C SOLAR | 17INR0020c |  | PECOS | SOLAR | WEST | 2019 | 0
722 | RE MAPLEWOOD 2D SOLAR | 17INR0020d |  | PECOS | SOLAR | WEST | 2020 | 0
723 | RE MAPLEWOOD 2E SOLAR | 17INR0020e |  | PECOS | SOLAR | WEST | 2020 | 0
724 | UPTON SOLAR | 16INR0114 |  | UPTON | SOLAR | WEST | 2018 | 0
725 | WEST OF PECOS SOLAR | 14INR0044 |  | REEVES | SOLAR | WEST | 2017 | 0
726 | Planned Capacity Total (Solar) | [6 empty] | 529
727 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 63
728
729 | Mothballed Resources
730 | GREENS BAYOU STG U5 |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON | 2016 | 371
731 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 1977 | 430
732 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 1978 | 420
733 | S R BERTRON CTG 2 (SINCE 5/15/2013) |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13
734 | S R BERTRON U1 (SINCE 5/15/2013) |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118
735 | S R BERTRON U2 (SINCE 5/15/2013) |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174
736 | S R BERTRON U3 (SINCE 5/22/2013) |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211
737 | S R BERTRON U4 (SINCE 5/22/2013) |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211
738 | Total Mothballed Capacity | [6 empty] | 1948
739
740 | Retiring Resources Unavailable to ERCOT (since last SARA report)
741 | [7 empty] | 0
742 | Total Retiring Capacity | [6 empty] | 0

## Background
Release Date: May 2, 2017
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a one-in-ten-years loss-of-load event criteria on a probabilistic basis.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
In contrast to the Capacity, Demand and Reserves (CDR) report, which addresses the sufficiency of planning reserves on an annual basis as described above, the SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. Consequently, load reduction resources included in the CDR report, such as Emergency Response Service (ERS) and Load Resources that provide operating reserves (LRs), are excluded from the SARA.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur, and thus help fulfill the reporting requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). Several sensitivity analyses are developed by varying the value of certain parameters that affect resource adequacy. The variation in these parameters is based on historic values of these parameters or adjustments by any known or expected changes.