| NPRR Number |  | NPRR Title | Resource Limits in Providing Responsive Reserves Service |
| --- | --- | --- | --- |
| Date Posted |  |  |  |
| Requested Resolution |  | Normal |  |
| Nodal Protocol Sections Requiring Revision |  | 3.18, Resource Limits in Providing Ancillary Service |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This NPRR changes the Resource Limits in Providing Responsive Reserves Service from a hard set upper limit of 20% of the unit capacity to a limit that is set by the actual performance of the unit. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | Describe qualitative benefits (Examples: satisfies regulatory requirements, data transparency enhancement, etc.), quantitative benefits (benefit calculations), impacts to market segments and other information relating to the impacts or benefits of the NPRR. |  |

| Sponsor |  |
| --- | --- |
| Name | Robert Helton |
| E-mail Address | Robert.helton@dynegy.com |
| Company | Dynegy Inc. |
| Phone Number | 832-435-7815 |
| Cell Number | 713-767-5174 |
| Market Segment | Independent Generator |

| Market Rules Staff Contact |  |
| --- | --- |
| Name |  |
| E-Mail Address |  |
| Phone Number |  |

Proposed Protocol Language Revision

- 3.18	Resource Limits in Providing Ancillary Service

(1)	For both Generation Resources and Load Resources the High Sustained Limit (HSL) must be greater than or equal to the Low Sustained Limit (LSL) and the sum of the Resource-specific designation of capacity to provide Responsive Reserve (RRS), Regulation Up (Reg-Up), Regulation Down (Reg-Down), and Non-Spinning Reserve (Non-Spin).

(2)	For Non-Spin, the amount of Non-Spin provided must be less than or equal to the HSL for Off-Line Generation Resources.

(3)	For RRS Service:

  - Each Resource providing RRS must be On-Line and must be immediately responsive to system frequency.  A new or previously disqualified Resource seeking RRS qualification shall be qualified for providing RRS up to a capacity level demonstrated in  Responsive Reserve Ancillary Service testing as specified in Section 8.1.1.2.1.2.  The full amount of RRS provided from a Generation Resource shall not exceed 10 times the Emergency Ramp Rate of the Resource.

  - Hydro Generation Resources operating in the synchronous condenser fast-response mode may qualify to provide RRS up to the hydro Generation Resource’s proven  20-second response capability (which may be 100% of the HSL).  The initiation setting of the automatic under-frequency relay shall not be lower than 59.90 Hz;

  - Any QSE providing RRS shall be capable of receiving ERCOT telemetered control deployments from SCED.  A QSE shall be capable of updating its Resource’s RRS Ancillary Service Schedule within 15 seconds following ERCOT deployment instructions.

  - Generation Resources providing RRS shall have their Governors in service with their settings as specified by North American Electric Reliability Corporation (NERC) Reliability Standard BAL-001-TRE-1, Primary Frequency Response in the ERCOT Region.

  - Each QSE shall ensure that each Resource is able to meet the Resource’s obligations to provide its Ancillary Service Resource Responsibility.

  - For any hydro Generation Resource with a 5% of less droop setting operating as a generator, the amount of RRS provided  may never be more than 20% of the HSL. .

  - A Private Use Network with registered Resources may use the gross HSL for qualification and establishing a limit on the amount of RRS capacity that the Resources within the Private Use Network can provide.

  - In qualifying and establishing limits on Resources for providing RRS, ERCOT will consider the performance abilities and limitations of the technology of each Resource seeking to qualify as a RRS provider. Because qualification requirements for different technologies may reflect their technical capabilities and limitations, ERCOT may impose other administrative limitations, including but not limited to setting a maximum limit of the total amount of capacity reservation that can be awarded to each type of Resource technology.  ERCOT shall provide to the QSE the technical basis for any limitation imposed on a Resource for providing RRS.

(i)	The amount of RRS provided from a Load Resource must be less than or equal to the HSL minus the sum of the LSL, Reg-Up Resource Responsibility, Reg-Down Resource Responsibility, and Non-Spin Resource Responsibility.

- 8.1.1.2.1.2	Responsive Reserve Service Qualification

(1)	RRS may be provided by:

(a) 	Unloaded Generation Resources that are On-Line;

(b) 	Load Resources controlled by high-set under-frequency relays;

(c) 	Hydro RRS; or

(d) 	Controllable Load Resources.

(2)	The amount of RRS provided by individual Generation Resources and Controllable Load Resources is specified in the Operating Guides.  Each Resource providing RRS must be On-Line and capable of ramping the Resource’s Ancillary Service Resources Responsibility for RRS within ten minutes of the notice to deploy RRS, must be immediately responsive to system frequency, and must be able to maintain the scheduled level of deployment for the period of service commitment.  The amount of RRS on a Generation Resource may be further limited by requirements of the Operating Guides.

(3)	A QSE’s Load Resource must be loaded and capable of unloading the scheduled amount of RRS within ten minutes of instruction by ERCOT and must either be immediately responsive to system frequency or be interrupted by action of under-frequency relays with settings as specified by the Operating Guides.

(4)	Any QSE providing RRS shall provide communications equipment to receive ERCOT telemetered control deployments of RRS.

(5)	Generation Resources providing RRS shall have their governors in service.

(6)	Load Resources on high-set under-frequency relays providing RRS must provide a telemetered output signal, including breaker status and status of the under-frequency relay.

(7)	Each QSE shall ensure that each Resource is able to meet the Resource’s obligations to provide the Ancillary Service Resource Responsibility.  Each Generation Resource and Load Resource providing RRS must meet additional technical requirements specified in this Section.

(8)	A qualification test for each Resource to provide RRS is conducted during a continuous eight-hour period agreed to by the QSE and ERCOT.  ERCOT shall confirm the date and time of the test with the QSE.  ERCOT shall administer the following test requirements:

(a)	At any time during the window (selected by ERCOT when market and reliability conditions allow and not previously disclosed to the QSE), ERCOT shall notify the QSE it is to provide an amount of RRS from its Resource to be qualified equal to the amount that the QSE is requesting qualification.  The QSE shall acknowledge the start of the test.

(b)	For Generation Resources desiring qualification to provide RRS, ERCOT shall send a signal to the Resource’s QSE to deploy RRS, indicating the MW amount.  ERCOT shall monitor the QSEs telemetry of the Resource’s Ancillary Service Schedule for an update within 15 seconds.  ERCOT shall measure the test Resource’s response as described under Section 8.1.1.4.2, Responsive Reserve Service Energy Deployment Criteria.  ERCOT shall evaluate the response of the Generation Resource given the current operating conditions of the system and determine the Resource’s qualification to provide RRS.

(i)	For the 10-minute duration of the test, when market and reliability conditions allow, the ERCOT Control Area Operator shall send steady sequence of increasing ramp control signals to the QSE for a specific Resource such that the full amount of requested RRS capacity is deployed in 10 minutes.  ERCOT shall maintain a duration interval of no less than 10 minutes.  The control signals may not request Resource performance beyond the HSL, LSL, and ramp rate limit agreed on prior to the test.

(ii)	ERCOT shall measure and record the average real power output for each minute of the Resource(s) being tested represented by the QSE.  During test, the Generation/Controllable Load Resource Energy Deployment Performance (GREDP/CLREDP) calculated in accordance with Section 8.1.1.4.1, Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance, over the entire 10 minute interval must be less than or equal to 5%.

(iii)	In lieu of conducting a RRS test, a Resource may be qualified for an amount of RRS equivalent to an amount no greater than Reg-Up successfully demonstrated under the Regulation Service Qualification testing procedures in Section 8.1.1.2.1.1.

(c)	For Controllable Load Resources desiring qualification to provide RRS, ERCOT shall send a signal to the Resource’s QSE to deploy RRS, indicating the MW amount.  ERCOT shall measure the test Resource’s response as described under Section 8.1.1.4.2.  ERCOT shall evaluate the response of the Controllable Load Resource given the current operating conditions of the system and determine the Controllable Load Resource’s qualification to provide RRS.

(d)	For Load Resources, excluding Controllable Load Resources, desiring qualification to provide RRS, ERCOT shall deploy RRS, indicating the MW amount.  ERCOT shall measure the test Resource’s response as described under Section 8.1.1.4.2.

(e)	On successful demonstration of all test criteria, ERCOT shall qualify that the Resource is capable of providing RRS and shall provide a copy of the certificate to the QSE and the Resource Entity.