## Slide 1: PSCAD models

## Slide 2: Time vs . Phasor or Domain Simulation
EMTDC is most suitable for simulating the time domain instantaneous responses (also popularly known as electromagnetic transients) of electrical systems.
EMTDC represents and solves differential equations (for both electromagnetic and electromechanical systems) in the time domain. Solutions are calculated based on a fixed time step, and its program structure allows for the representation of control systems, either with or without electromagnetic or electromechanical systems present - can duplicate the response of the power system at all frequencies, bounded only by the user-selected time step.
Phasor domain solution engines, such as load-flow and transient stability programs utilize steady-state equations to represent electrical circuits - can output only fundamental frequency magnitude and phase information.

## Slide 3: EMTDC model run on PSCAD
EMTDC electromagnetic transient simulation engine for power systems – that is there are other program that can be used by group.
PSCAD is a CAD type software to run EMTDC solutions – this software needs to be called out as our standard - PSCAD version 4.5.3
PSCAD enables the user to schematically construct a circuit, run a simulation, analyze the results, and manage the data in a completely integrated, graphical environment – probable the best choice
  Online plotting functions, controls and meters are also included, enabling the user to alter system parameters during a simulation run, and thereby view the effects while the simulation is in progress

## Slide 4: What is the concern?
EMTDC users can write in Fortran, C and MATLAB – develop standard
OEM protect this information because it gives other OEM insight into how their equipment is constructed - We need permission to share models and data within ERCOT
Question: what do we have now?
Develop a standard requirement and modify NDA to allow sharing within ERCOT.

## Slide 5: Model Specification
1. Be compatible with PSCAD version 4.5.3.
2. Represent the full detailed inner control loop of the power electronics. The model cannot use the same approximations classically used in transient stability modeling, and should fully represent all fast inner controls, as implemented in the real equipment. It is possible to create models which embed the actual hardware code into a PSCAD component, and this is the best type of model.
3. Represent plant level controllers as they are implemented in the real controls. Operating modes that require system specific adjustment should be user accessible. In particular, plant level voltage control should be represented along with adjustable droop characteristics to help in analyzing voltage control coordination.
4. Represent all pertinent control features as they are implemented in the real controls (e.g. PLLs, etc.)
5. Represent SSR mitigation and/or protection including the ability to enable and disable SSR mitigation/protection, if applicable

## Slide 6: Model Specification (cont.)
6. Represent dynamic reactive devices including automatically controlled capacitor and reactor banks, if applicable.
7. Represent all pertinent electrical and mechanical configurations, such as filters and specialized transformers, gearboxes, torsional models. The model can be either a full IGBT representation, or use a voltage source interface that mimics the IGBT operation (unless harmonic studies require full representation of switching dynamics). Current source interface is not recommended.
8. Have all pertinent protections modeled in detail. Typically this includes various over-voltage and under-voltage protections, frequency protections, DC bus voltage protections, and overcurrent protection. There may be others.
9.Include model flags for protection and trip diagnostics that clearly identify why a model trips during simulations.
10. Allow various dispatch levels and accurately reflect behavior throughout the valid MW output range from minimum power through maximum power.

## Slide 7: Model Specification (cont.)
11. Have pertinent control or hardware options accessible to the user.
12. Initialize as quickly as possible (<1-3 seconds) to user supplied terminal conditions.
13. Be capable of running at a minimum time step of 20 us, unless specific control parameters require smaller. Most of the time, requiring a smaller time step means that the control implementation has not used the interpolation features of PSCAD, or is using inappropriate interfacing between the model and the larger network. Lack of interpolation support introduces inaccuracies into the model at higher time steps.
14. Support multiple instances of the model in the same simulation, Support the PSCAD “snapshot” feature, Support the PSCAD “multiple run” feature.