## Purpose and Background
NERC LIST OF ACCEPTABLE MODELS FOR INTERCONNECTION-WIDE MODELING
Purpose
The purpose of this list of acceptable models is to develop and maintain a repository of models deemed acceptable by the ERO and industry stakeholders for use in developing interconnection-wide models developed by the MOD-032 Designee. The NERC System Analysis and Modeling Subcommittee (SAMS) maintains and coordinates activities to address any modeling issues and will reflect any updates in this list of acceptable models on a periodic basis, or as needed.
This list seeks to bring together multiple sources of data to ensure uniformity in the use of models across interconnections. While models may be deemed 'obsolete' or 'deprecated' due to known issues, those models are not removed from the software vendor libraries for various reasons. However, those models should not be used for developing interconnection-wide models.
Table Legend
Yellow: Use of this model is not recommended. Other models may be more appropriate for use. While existing models in the cases may still use these models, their future use is discouraged. Resubmission of models as per MOD-026-1 and MOD-027-1 for existing resources should convert the existimg model to a more representative model.
Orange: Use of this model for new resources or resources re-certifying their models as per MOD-026-1 and MOD-027-1 should be prohibited, unless specifically acceptable by the Modeling Designee for interconnection-wide base case creation. Known modeling issues, errors, or deficiencies exist with this model. Modeling Designees should consider proactive actions to move towards more representative and accurate models.
Disclaimers and Notes
> Some of the models in this list may not be acceptable for use by all Modeling Designees. Modeling requirements as specified for each interconnection by the Modeling Designees supercede this list and those Designees should be consulted directly.
> This list of models may not be comprehensive of all models available in the various commercial software platforms. Additional models may exist in the software platforms and are not addressed in this list of acceptable models.
> 'Black box' models (e.g., no block diagrams, documentation, proprietary models, etc.) are prohibited for use in interconnection-wide models.
> User-defined models are acceptable; however, where a generic model can accurately represent the resource (e.g., wind power plants), the generic model should be used. Some exceptions to this exist such as HVDC circuits.
Questions
Please direct any questions to NERC System Analysis (SystemAnalysis@nerc.net).

## NERC Acceptable Models List
NERC LIST OF ACCEPTABLE MODELS FOR INTERCONNECTION-WIDE MODELING
Last Updated: February 2017
Use of this model is not recommended. Other models are more suitable.
Future use of this model should be prohibited. Modeling limitations or discrepancies known.
Machine Models
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 16) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
Round Rotor Generator Model (IEEE Std 1110 §5.3.2 Model 2.2) | GENROU | genrou | X | X | X | X | X | X
Salient Pole Generator Model (IEEE Std 1110 §5.3.1 Model 2.1) | GENSAL | gensal | X | X | X | X | X | X
Round Rotor Generator Model (IEEE Std 1110 §5.3.2 Model 2.2) | GENROE | -- | X | -- | X | -- | X | --
Salient Pole Generator Model (IEEE Std 1110 §5.3.1 Model 2.1) | GENSAE | -- | X | -- | X | -- | X | --
Round Rotor Generator with DC Offset Torque Component | GENDCO | gensdo | X | -- | -- | -- | -- | --
Cross Compound WECC Type F | -- | gencc | -- | X | -- | X | -- | X
Generator Type F | -- | gentpf | -- | X | -- | X | -- | X
Generator Type J | GENTPJU1 | gentpj | -- | X | X | X | -- | X
Classical Generator Model (IEEE Std 1110 §5.4.2) | GENCLS | gencls | X | X | X | X | X | X | Simplistic representation.
Third Order Generator Model | CGEN1 | -- | -- | -- | X | -- | -- | -- | Simplistic representation.
Transient Level Generator Model | GENTRA | -- | X | -- | X | -- | -- | -- | Simplistic representation.
Salient Pole Frequency Changer Model | FRECHG | -- | -- | -- | -- | -- | -- | --
"Two-cage" or "One-Cage" Induction Generator | CIMTR1, CIMTR3 | genind | X | X | -- | -- | -- | --
Signal Playback Models
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 15) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
Play-In of Voltage and/or Frequency Signal | PLBVFU1 | -- | X | -- | X | X | -- | --
Frequency Playback Model | TSTGOV1 | -- | X | -- | X | X | -- | --
Play-In of Generator Field Voltage | -- | plefd | X | -- | X | X | -- | --
Delivers Played-In Signal to Dynamic Simulation Models | -- | plnow | -- | -- | X | X | -- | --
Play-In of Voltage Regulator and Governor Reference Settings | -- | plref | X | -- | X | X | -- | --
Play-In Turbine Power | -- | pltp | X | -- | X | X | -- | --
Thevenin Source of Defined Voltage Amplitude and Frequency | -- | gthev | -- | -- | X | X | -- | --
Renewable Energy Resource Models
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 15) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
Generic Type 1 WTG Generator Model (Fixed-speed induction generator) | WT1G1 | wt1g | X | X | X | X | X | X
Generic Type 2 WTG Generator Model (Variable slip induction generator with variable rotor resistance) | WT2G1 | wt2g | X | X | X | X | X | X
Generic Type 3 WTG Generator/Converter Model - PSSE (Doubly-fed induction generator) | WT3G1 | -- | X | -- | X | -- | X | -- | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 3 WTG Generator/Converter Model - PSLF (Doubly-fed induction generator) | WT3G2 | wt3g | X | X | X | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 4 WTG Generator/Converter Model - PSSE (Variable speed generator with full converter) | WT4G1 | -- | X | -- | X | -- | X | -- | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 4 WTG Generator/Converter Model - PSLF (Variable speed generator with full converter) | WT4G2 | wt4g | -- | X | -- | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 2 WTG Rotor Resistance Control Model | WT2E1 | wt2e | X | X | X | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 3 WTG Electrical Control Model | WT3E1 | wt3e | X | X | X | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 4 WTG Electrical Control Model - PSSE | WT4E1 | -- | X | -- | X | -- | X | -- | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 4 WTG Electrical Control Model - PSLF | WT4E2 | wt4e | -- | X | -- | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 1 Two Mass Turbine Model | WT12T1 | wt1t | X | X | X | X | X | X
Generic Type 2 Two Mass Turbine Model | WT12T1 | wt2t | X | X | X | X | X | X
Generic Type 3 WTG Turbine Model | WT3T1 | wt3t | X | X | X | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 3 and 4 WTG Drive Train Model | WTDTAU1 | wtgt_a | X | X | X | X | X | X
Generic Type 3 WTG Pitch Control Model | WT3P1 | wt3p | X | X | X | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 3 and 4 WTG Pitch Control Model | WTPTAU1 | wtgp_a | X | X | X | X | X | X
Generic Type 1 and 2 WTG Pitch Control Model | WT12A1 | wt1p | X | X | X | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 2 and 2 WTG Pitch Control Model | -- | wt1p_b | -- | X | -- | -- | -- | --
Generic Type 3 and 4 WTG Aerodynamics Model | WTARAU1 | wtga_a | X | X | X | X | X | X
Generic Type 3 and 4 WTG Torque Control Model | WTTQAU1 | wtgq_a | X | X | X | X | X | X
Generic Type 4 WTG Power Converter Model | -- | wt4t | -- | X | -- | X | -- | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Generic Type 4 Pitch Control Model | -- | wt4p | -- | -- | -- | X | -- | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Linearized Model of PV Panel Output Curve | PANELU1 | -- | -- | -- | -- | -- | -- | --
Linearized Model of PV Panel Solar Irradiance Profile | IRRADU1 | -- | -- | -- | -- | -- | -- | --
Generic Phase 2 Renewable Energy Generator/Converter Model | REGCAU1 | regc_a | X | X | X | X | -- | --
Generic Phase 2 Renewable Energy Electrical Controls Model | REECAU1 | reec_a | X | X | X | X | X | X
Generic Phase 2 Renewable Energy Plant Controller | REPCAU1 | repc_a | X | X | X | X | X | X
Generic Phase 2 PV Electrical Controls Model | REECBU1 | reec_b | X | X | X | X | X | X
Generic Phase 2 Energy Storage Electrical Controls | -- | reec_c | -- | X | -- | X | -- | --
Generic Phase 2 Renewable Energy Auxiliary Control Model | REAX4BU1 | -- | -- | -- | -- | -- | -- | --
Vestas Model of Wound-Rotor Induction Generator (with Variable External Rotor Resistance) | -- | genwri | -- | X | -- | X | -- | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Vestas Model of Rotor Resistance Control for Wound-Rotor Induction WTG | -- | exwtg1 | -- | X | -- | X | -- | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
GE Wind Turbine Control Model - Doubly Fed Induction Generator (DFIG) and Full Converter (FC) Models | -- | wndtge | -- | X | -- | X | -- | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
GE Wind Turbine Generator/Converter - DFAG and FC Models | -- | gewtg | -- | X | -- | X | -- | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
GE Wind Turbine Excitation (converter) Control Model for DFAG Generators | -- | exwtge | -- | X | -- | X | -- | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
GE Wind Turbine Plant-Level Supervisory Voltage/VAR Control | -- | wndvar | -- | -- | -- | -- | -- | -- | 2nd Generation Renewable Models replace these; numerical issues in base cases.
Solar Photovoltaic Generator/Converter Model | PVGU1 | pv1g | -- | X | -- | X | -- | --
Solar Photovoltaic Electrical Control Model | PVEU1 | pv1e | -- | X | -- | X | -- | --
Distributed photovoltaic system | -- | pvd1 | -- | X | -- | -- | -- | --
Excitation System Models
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 15) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
IEEE Std 421.5 Type AC1A | ESAC1A | esac1a | X | X | X | X | X | X
Modified IEEE Std 421.5 Type AC1A | ESURRY | -- | -- | -- | X | -- | X | --
IEEE Std 421.5 Type AC2A | ESAC2A | esac2a | X | X | X | X | X | X
IEEE Std 421.5 Type AC3A | ESAC3A | esac3a | X | X | X | X | X | X
IEEE Std 421.5 Type AC4A | ESAC4A | esac4a | X | X | X | X | X | X
IEEE Std 421.5 Type AC5A | ESAC5A | esac5a | X | X | X | X | X | X
IEEE Std 421.5 Type AC6A | ESAC6A | esac6a | X | X | X | X | X | X
Modified IEEE Std 421.5 Type AC6A (added speed multiplier) | USAC6AU | exac6a | -- | X | -- | -- | -- | --
IEEE Std 421.5 Type AC7B* | AC7B | esac7b | X | X | X | X | X | X
IEEE AC7B Excitation System Model w/ OEL for Brushless Exciters and GE EX2100 Controls | -- | ex21br | -- | -- | -- | -- | -- | --
IEEE Std 421.5 Type AC8B | AC8B | esac8b | X | X | X | X | X | X
Modified IEEE Std 421.5 Type AC8B | ESAC8B | exac8b | X | X | X | X | X | X
IEEE Std 421.5 Type DC1A | ESDC1A | esdc1a | X | X | X | X | X | X
IEEE Std 421.5 Type DC2A | ESDC2A | esdc2a | X | X | X | X | X | X
IEEE Std 421.5 Type DC3A | DC3A | esdc3a | X | X | X | X | X | X
IEEE Std 421.5 Type DC4B | DC4B | esdc4b | X | X | X | X | X | X
IEEE Std 421.5 Type ST1A | ESST1A | esst1a | X | X | X | X | X | X
IEEE Std 421.5 Type ST2A | ESST2A | esst2a | X | X | X | X | X | X
IEEE Std 421.5 Type ST3A | ESST3A | esst3a | X | X | X | X | X | X
IEEE Std 421.5 Type ST4B | ESST4B | esst4b | X | X | X | X | X | X
Modified IEEE Std 421.5 Type ST4B (without OEL & UEL inputs and Vgmax) | -- | exst4b | -- | X | -- | X | -- | X
IEEE Std 421.5 Type ST5B** | ST5B | esst5b | X | X | X | X | X | X
IEEE Proposed Type ST5B Excitation System | URST5T | -- | X | -- | X | -- | X | --
IEEE Std 421.5 Type ST6B | ST6B | esst6b | X | X | X | X | X | X
IEEE Std 421.5 Type ST7B | ST7B | esst7b | X | X | X | X | X | X
1968 IEEE Type 1 | IEEET1 | ieeet1 | X | X | X | X | X | X
Modified 1968 IEEE Type 1 | IEET1A | -- | X | -- | X | -- | X | --
Modified 1968 IEEE Type 1 | IEET1B | -- | X | -- | X | -- | X | --
1968 IEEE Type 2 | IEEET2 | -- | X | -- | X | -- | X | --
1968 IEEE Type 3 | IEEET3 | -- | X | -- | X | -- | X | --
1968 IEEE Type 4 | IEEET4 | exdc4 | X | X | X | X | X | --
Modified 1968 IEEE Type 4 | IEEET5 | -- | X | -- | X | -- | X | --
Modified 1968 IEEE Type 4 | IEET5A | -- | X | -- | X | -- | X | --
1981 IEEE Type AC1 | EXAC1 | exac1 | X | X | X | X | X | X
Modified 1981 IEEE Type AC1 (modified rate feedback source and with added speed multiplier) | EXAC1A | exac1a | X | X | X | X | X | X
Modified 1981 IEEE Type AC1 | -- | exac1m | -- | -- | -- | -- | -- | --
1981 IEEE Type AC2 | EXAC2 | exac2 | X | X | X | X | X | X
1981 IEEE Type AC3 | EXAC3 | exac3 | X | X | X | X | X | --
Modified 1981 IEEE Type AC3 | ESAC3A | exac3a | -- | X | -- | X | -- | X
1981 IEEE Type AC4 | EXAC4 | exac4 | X | X | X | X | X | X
1981 IEEE Type DC1 | IEEEX1 | exdc1 | X | X | X | X | X | X
Modified 1981 IEEE Type DC1 | IEEEX2 | -- | X | -- | X | -- | X | --
Modified 1981 IEEE Type DC1 | IEEX2A | -- | X | -- | X | -- | X | --
1981 IEEE Type DC2 | EXDC2 | exdc2a | X | X | X | X | X | X
Modified 1981 IEEE Type DC2 | IEEEX2 | exdc2 | -- | X | -- | X | -- | X
1981 IEEE Type DC3 | IEEEX4 | exdc4 | X | X | X | X | X | X
1981 IEEE Type ST1 | EXST1 | exst1 | X | X | X | X | X | X
1981 IEEE Type ST2 | EXST2 | exst2 | X | X | X | X | X | X
Modified 1981 IEEE Type ST2 | EXST2A | exst2a | X | X | X | X | X | X
Modified 1981 IEEE Type ST2 | IEEEX3 | -- | X | -- | X | -- | X | --
1981 IEEE Type ST3 | EXST3 | exst3 | X | X | X | X | X | X
Modified 1981 IEEE Type ST3 | ESST3A | exst3a | -- | X | -- | X | -- | X
General Purpose Rotating Excitation System Model | REXSYS | rexs | X | X | X | X | X | X
General Purpose Rotating Excitation System Model | REXSY1 | -- | X | -- | X | -- | X | --
Proportional/Integral Excitation System Model | EXPIC1 | expic1 | X | X | X | X | X | X
Manual Excitation Control with Field Circuit Resistance | -- | mexs | -- | X | -- | -- | -- | X
General Purpose Transformer Fed Excitation System | -- | texs | -- | X | -- | X | -- | X
Bus or Solid Fed SCR Bridge Excitation System Model | SCRX | scrx | X | X | X | X | X | X
Bus or Solid Fed SCR Bridge Excitation System Model Type NEBB (NVE) | EXNEBB | -- | -- | -- | -- | -- | -- | --
Bus or Solid Fed SCR Bridge Excitation System Model Type NI (NVE) | EXNI | -- | -- | -- | -- | -- | -- | --
Simplified Excitation System | SEXS | sexs | X | X | X | X | X | X
IVO Excitation System Model | IVOEX | exivo | X | X | X | -- | X | X
ELIN Excitation System | CELIN | -- | -- | -- | X | -- | X | --
Basler Static Voltage Regulator Feeding DC or AC Rotating Exciter | EXBAS | -- | X | -- | X | -- | X | --
Brown-Boveri Transformer-Fed Static Excitation System Model | BBSEX1 | exbbc | X | X | X | X | X | X
Static PI Transformer Fed Excitation System | EXELI | exeli | X | X | X | X | X | X
VATECH (ELIN) Static Excitation System with PSS | -- | exeli2 | -- | -- | X | -- | X | --
GE EX2000 Excitation System | EX2000 | -- | X | -- | X | -- | X | -- | Field current limiter latch issue. Replace with AC7B in PSSE and ex21br in PSLF. | NERC EX2000 Modeling Notification
AEP Rockport excitation system | EMAC1T | -- | X | -- | X | -- | X | --
Czech Proportional/Integral Excitation System Model | BUDCZT | -- | -- | -- | -- | -- | -- | --
High Dam Excitation System Model | URHIDT | -- | -- | -- | -- | -- | -- | --
Power System Stabilizer
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 15) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
Transient Excitation Boosting Stabilizer Model | BEPSST | -- | -- | -- | -- | -- | -- | --
Dual-Input Signal Power System Stabilizer Model | IEE2ST | -- | X | -- | X | -- | X | --
1981 IEEE Power System Stabilizer | IEEEST | ieeest | X | X | X | X | X | X
IVO Stabilizer Model | IVOST | -- | X | -- | -- | -- | -- | --
Ontario Hydro Delta-Omega Power System Stabilizer | OSTB2T | -- | -- | -- | X | -- | -- | --
Ontario Hydro Delta-Omega Power System Stabilizer | OSTB5T | -- | -- | -- | X | -- | -- | --
IEEE Std 421.5-2005 Single-Input Stabilizer Model | PSS1A | pss1a | X | X | -- | X | -- | X
1992 IEEE Type PSS2A Dual-Input Signal Stabilizer Model | PSS2A | pss2a | X | X | X | X | X | X
IEEE Std 421.5-2005 PSS2B Dual-Input Stabilizer Model | PSS2B | pss2b | X | X | X | X | X | X
IEEE Std 421.5-2005 Dual-Input Stabilizer Model | PSS3B | pss3b | -- | X | -- | X | X | X
IEEE Std 421.5-2005 Dual-Input Stabilizer Model | PSS4B | -- | -- | -- | -- | -- | -- | --
PTI Microprocess-Based Stabilizer Model | PTIST1 | -- | -- | -- | X | -- | X | --
PTI Microprocess-Based Stabilizer Model | PTIST3 | -- | -- | -- | X | -- | X | --
Speed Sensitive Stabilizer Model | STAB1 | -- | X | -- | X | -- | X | --
ASEA Power Sensitive Stabilizer Model | STAB2A | -- | X | -- | X | X | X | --
Power Sensitive Stabilizer Model | STAB3 | -- | X | -- | X | -- | X | --
Power Sensitive Stabilizer Model | STAB4 | -- | X | -- | X | -- | X | --
Dual-Input Signal Power System Stabilizer Model | ST2CUT | wsccst | X | X | X | X | X | X
Dual Input Stabilizer (IEEE Type PSS2A) + Voltage Boost Signal Transient Stabilizer and Vcutoff | -- | psssb | -- | X | -- | X | -- | X
WECC Supplementary Signal for Static Var System | STBSVC | -- | X | -- | X | -- | X | --
Synchronous Condenser Auxiliary Control Model | SYNAXBU1 | -- | -- | -- | -- | -- | -- | --
Single Input PSS for SVSMO1, SVSMO2, and SVSMO3 | -- | psssvc | -- | -- | -- | -- | -- | --
Current Compensation Models
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 15) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
Cross-Current Compensation Model with Reactive Current Feedback | CCOMP4U1 | ccomp4 | -- | X | -- | -- | -- | --
Voltage Regulator Compensating Model | COMP | ** | X | -- | X | -- | X | --
Cross and Joint Current Compensation Model | COMPCC | ccomp | X | X | -- | -- | X | --
IEEE Std 421.5 Current Compensator | IEEEVC | † | X | † | X | † | X | †
Remote Bus Voltage Signal Model | REMCMP | ** | X | -- | X | -- | X | --
† - Current compensator is part of the generator model
** - Built into generator model in PSLF
Turbine-Governor Models
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 15) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
Steam Plant Boiler Turbine-Governor Model | -- | ccbt1 | -- | X | -- | -- | -- | X
Combined Cycle Plant Steam Turbine Model | UCBGT | ccst3 | -- | -- | -- | -- | -- | X
GE Frame 6, 7, and 9 Gas Turbine Model | -- | gegt1 | -- | -- | -- | -- | -- | --
General Purpose (Gas Turbine & Single Shaft CC) Turbine-Governor Model | GGOV1 | ggov1 | X | X | X | X | X | X
General Governor Model with Frequency-Dependent Fuel Flow Limit | -- | ggov2 | -- | X | -- | -- | -- | X
General Governor Model with GE Gas Turbine Control Features | -- | ggov3 | -- | X | -- | X | -- | X
Hydro Turbine-Governor Model | -- | h6b | -- | -- | -- | X | -- | --
Model to Manage Parameter Data for h6b Hydro Turbine-Governor Model | -- | h6bd | -- | X | -- | -- | -- | --
Hydro Governor Model for up to 4 Units on Common Penstock | -- | hygov8 | -- | -- | -- | -- | -- | --
Hydro Turbine-Governor (plants w/ straightforward penstock config + PID governor, blade angle for Kaplan) | -- | hypid | -- | X | -- | -- | -- | --
Hydro Turbine w/ Woodward Electro-Hydraulic PID Governor, Penstock, Surge Tank, and Inlet Tunnel | -- | hyst1 | -- | -- | -- | -- | -- | --
LM 2500 Aero-Derivative Gas Turbine Governor Model | -- | lm2500 | -- | -- | -- | -- | -- | --
LM 6000 Aero-Derivative Gas Turbine Governor Model | -- | lm6000 | -- | -- | -- | -- | -- | --
Single Shaft Combined Cycle Plant Model | -- | stag1 | -- | -- | -- | -- | -- | --
Woodward 2301 Governor and Basic Turbine Model | -- | w2301 | -- | X | -- | X | -- | X
Brown-Boveri Turbine-Governor Model | BBGOV1 | -- | -- | -- | -- | -- | X | --
Cross Compound Turbine-Governor Model | CRCMGV | crcmgv | X | X | X | X | X | X
Woodward Diesel Governor Model | DEGOV | -- | X | -- | -- | -- | X | --
Woodward Diesel Governor Model | DEGOV1 | degov1 | X | -- | X | -- | X | --
Gas Turbine-Governor Model | GAST | -- | X | -- | X | -- | X | --
Gas Turbine-Governor Model | GAST2A | -- | X | -- | X | -- | X | --
Gas turbine-governor | GASTWD | -- | X | -- | X | -- | X | --
Hydro Turbine-Governor Model | HYGOV | hygov | X | X | X | X | X | X
Hydro Turbine-Governor Model | HYGOV2 | -- | X | -- | X | -- | X | --
Hydro Turbine-Governor Lumped Parameter Model | HYGOVM | -- | -- | -- | -- | -- | -- | --
Fourth Order Lead-Lag Hydro-Turbine Model | HYGOVR1 | hygovr | X | X | X | X | X | X
Hydro Turbine-Governor Traveling Wave Model | HYGOVT | -- | -- | -- | -- | -- | -- | --
1981 IEEE Type 1 General Steam Turbine-Governor Model | IEEEG1 | -- | X | -- | X | -- | X | --
1981 IEEE Type 2 General Approx. Linear Ideal Hydro Model | IEEEG2 | -- | X | -- | X | -- | X | --
1981 IEEE Type 3 General Mechanical-Hydraulic Model | IEEEG3 | ieeeg3 | X | X | X | X | X | X
Hydro Turbine-Governor (plants with straightforward penstock config + hydraulic govs of 'dashpot' type) | IEEEG3 | hygov4 | -- | X | -- | X | -- | X
1973 IEEE General Steam Non-Reheat | IEESGO | -- | X | -- | X | -- | X | --
IVO Turbine-Governor Model | IVOGO | -- | -- | -- | -- | -- | X | --
Hydro Turbine-Governor Model | PIDGOV | pidgov | X | X | X | X | X | X
Pratt & Whitney Turboden Turbine-Governor Model | PWTBDU1 | -- | -- | -- | -- | -- | -- | --
Torsional-Elastic Shaft Model for 25 Masses | SHAF25 | -- | -- | -- | -- | -- | -- | --
Steam Turbine-Governor Model | TGOV1 | tgov1 | X | X | X | X | X | X
Steam Turbine-Governor Model w/ Fast Valving | TGOV2 | -- | X | -- | X | -- | X | --
1973 Modified IEEE Type 1 General Steam Turbine-Governor Model w/ Fast Valving | TGOV3 | tgov3 | X | X | X | X | X | X
Modified IEEE Type 1 General Steam Turbine-Governor Model w/ PLU and EVA | TGOV4 | -- | -- | -- | -- | -- | -- | --
Modified IEEE Type 1 General Steam Turbine-Governor Model w/ Boiler Controls | TGOV5 | -- | X | -- | -- | -- | X | --
Czech Hydro or Steam Turbine-Governor Model | TURCZT | -- | -- | -- | -- | -- | -- | --
Tail Water Depression Hydro Governor Model 1 | TWDM1T | -- | -- | -- | -- | -- | -- | --
Tail Water Depression Hydro Governor Model 2 | TWDM2T | -- | -- | -- | -- | -- | -- | --
Combined Cycle - Single Shaft Turbine-Governor Model | URCSCT | -- | -- | -- | -- | -- | -- | --
WECC Gas Turbine Governor Model | URGS3T | gast | X | X | X | X | X | X | Simplistic representation of steam turbine-governor system. Insufficient model capability of modern digital controls.
Woodward Electronic Hydro Governor Model | WEHGOV | -- | X | -- | X | -- | X | --
Westinghouse Digital Governor Model for Gas Turbines | WESGOV | -- | X | -- | X | -- | X | --
Woodward PID Hydro Governor Model | WPIDHY | -- | X | -- | X | -- | X | --
WECC Double Derivative Hydro Governor Model | WSHYDD | g2wscc | X | X | X | X | X | X
WECC GP Hydro Turbine-Governor Model | -- | gpwscc | X | X | X | X | X | X | Use hyg3 or WSHYGP model. | WECC approved model list
PID Governor, Double-Derivative Governor, and Turbine (WECC GP governor, WECC G2 turbine-governor) | WSHYGP | hyg3 | -- | X | -- | X | -- | X
Modified IEEE Type 1 General Steam Turbine-Governor Model w/ Speed Deadband | WSIEG1 | ieeeg1 | X | X | X | X | X | --
Load Controller Models
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 15) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
Turbine Load Controller Model | LCFB1 | lcfb1 | X | X | X | X | X | X
Load Models
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 15) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
Induction Generator Model with Rotor Flux Transients | CIMTR1 | -- | X | -- | X | -- | X | --
Induction Motor Model with Rotor Flux Transients | CIMTR2 | -- | X | -- | X | -- | X | --
Induction Generator Model with Rotor Flux Transients | CIMTR3 | genind | X | -- | X | -- | X | --
Induction Motor Model with Rotor Flux Transients | CIMTR4 | motor1 | X | X | X | X | X | X
Induction Motor Model | CIM5BL | -- | -- | -- | -- | -- | -- | --
Induction Motor Model | CIM6BL | -- | -- | -- | -- | -- | -- | --
Induction Motor Model | CIMWBL | motorw | -- | X | X | X | X | X
IEEE Load Model | IEEL__ | _lwscc | X | -- | X | X | X | --
Load Frequency Model | LDFR__ | -- | X | -- | X | -- | X | --
Extended-Term Load Reset Model | EXTLBL | -- | -- | -- | -- | -- | -- | --
Complex Load Model | CLOD__ | -- | X | -- | X | -- | X | --
Composite Load Model | CMLDBLU1 | cmpldw | -- | X | X | X | X | X
Composite Load Model w/ DER Component | -- | cmpldwg | -- | -- | -- | -- | -- | --
Composite Load Model w/ Modular Capability | -- | cmpldw2 | -- | X | -- | -- | -- | --
Performance-Based Model of Single Phase Air Conditioner Motor Model | ACMTBLU1 | ld1pac | -- | X | -- | -- | -- | --
Phasor Model of Single-Phase Air-Conditioner Compressor Motor | -- | motorc | -- | X | -- | -- | -- | -- | Experimental model. | PSLF Manual
* | COMP: PSSE: Area-based: __=AR; Bus-based: __=BL; Zone-based: __=ZN; All: __=AL
* | COMP: PSLF: Area-based: __=a; Bus-based: __=b; Zone-based: __=z; All: __=w
Static Var Systems and FACTS
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 15) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
WECC Generic Continuous Control SVC Model | SVSMO1U2 | svsmo1 | -- | X | X | X | -- | X
WECC Generic Discrete Control SVC Model | SVSMO2U2 | svsmo2 | -- | X | X | X | -- | X
WECC Generic STATCOM-Based SVC Model | SVSMO3U2 | svsmo3 | -- | X | X | X | -- | X
SCR Controlled Static VAR Source Model | CSVGN1 | -- | X | -- | X | -- | X | --
SCR Controlled Static VAR Source Model | CSVGN3 | -- | X | -- | X | -- | X | --
SCR Controlled Static VAR Source Model | CSVGN4 | -- | X | -- | X | -- | X | --
WECC Controlled Static VAR Source Model | CSVGN5 | vwscc | X | X | X | X | X | X
WECC Controlled Static VAR Source Model | CSVGN6 | -- | X | -- | X | -- | -- | --
Switched Shunt Model | SWSHNT | msc1 | X | X | X | -- | -- | --
American Superconductor DSMES Device | CDSMS1 | -- | -- | -- | -- | -- | -- | --
Static Condenser FACTS Model | CSTATT | -- | X | -- | X | -- | X | --
Static Condenser (modeled as FACTS in power flow) | CSTCNT | -- | -- | -- | X | -- | -- | --
ABB SVC Model | ABBSVC1 | -- | -- | -- | X | -- | -- | --
SVC for Switched Shunt | CHSVCT | -- | -- | -- | X | -- | X | --
SVC for Switched Shunt | CSSCST | -- | X | -- | X | -- | X | --
EPRI Superconducting Electromagnetic Energy Storage FACTS Model | CSMEST | -- | -- | -- | -- | -- | -- | --
EPRI Battery Energy Storage FACTS Model | CBEST | -- | X | -- | -- | -- | X | --
Protection and Other Models
Model Description | Siemens PTI (v. 33) | GE PSLF (v. 19) | PowerWorld Simulator (v.19) |  | PowerTech DSATools (v. 15) |  | V&R Energy POM (2015) |  | Comments | Reference
|  |  | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
Generic Generator Protection System | -- | gp1 | -- | X | -- | X | -- | X
Generic Generator Protection System | -- | gp2 | -- | X | -- | -- | -- | X
Under-/Over-Frequency Generator Bus Disconnection Relay | FRQTPAT | lhfrt | X | X | X | X | -- | X
Under-/Over-Frequency Generator Trip Relay | FRQDCAT | -- | X | -- | X | -- | -- | --
Under-/Over-Voltage Generator Bus Disconnection Relay | VTGTPAT | lhvrt | X | X | X | X | X | X
Under-/Over-Voltage Generator Trip Relay | VTGDCAT | -- | X | -- | X | -- | X | --
Time-Inverse Overcurrent Relay | TIOCR1 | locti | X | X | x | -- | X | X
Definite Time Underfrequency Load Shedding Relay | LDS3BL | lsdt1 | X | X | X | X | -- | X
Definite Time Undervoltage Load Shedding Relay | LDS3BL | lsdt2 | -- | X | X | X | -- | X
Definite Time Undervoltage Load Shedding Relay | LDS3BL | lsdt9 | -- | X | X | X | -- | X
Out-of-Step Relay with 3 Zones (Lens, Tomato, or Circle) | -- | ooslen | -- | X | -- | -- | -- | X
Out-of-Step Relay with 3 Zones (Lens, Tomato, Circle, or Rectangle) | -- | ooslnq | -- | X | -- | -- | -- | --
Out-of-Step Mho Relay with Blinders | -- | oosmho | -- | X | -- | -- | -- | --
Metal Oxide Varistor and Bypass Protection for Series Capacitor | -- | scmov | -- | X | -- | -- | -- | --
Switched Capacitor Bank Model | SWCAPT | -- | -- | -- | -- | -- | -- | --
Mechanically Switched Capacitor | -- | msc1 | -- | X | -- | -- | -- | --
Mechanically Switched Reactor | -- | msr1 | -- | X | -- | -- | -- | --
Mechanically Switched Line Reactor | -- | mslr1 | -- | X | -- | -- | -- | --
Mechanically Switched Shunt | -- | mss1 | -- | -- | -- | -- | -- | --
Mechanically Switched Shunt | -- | mss2 | -- | -- | -- | -- | -- | --
Over-Excitation Limiter for Synchronous Machine Excitation System | -- | oel1 | -- | X | -- | X | -- | X
Load Tap Changer Model | OLTC1T | ltc1 | -- | X | -- | -- | -- | --
Variable Frequency Transformer or Rotary Phase Shift Regulator | OLPS1T | vft | -- | X | -- | -- | -- | --
Applicable Reference Materials and Additional Reading:
[1] "IEEE Guide for Synchronous Generator Modeling Practices and Applications in Power System Stability Analyses," IEEE Std 1110-2002.
[2] Undrill, J., "The gentpj model," November 19, 2007 (updated June 19, 2012). http://www.wecc.biz/
[3] "IEEE Recommended Practice for Excitation System Models for Power System Stability Studies," IEEE Std 421.5-2005.
[4] “Computer Representation of Excitation Systems," IEEE Transactions on Power Apparatus and Systems, Vol. PAS-87, No. 6, pp. 1460-1468, 1968 (Committee Report).
[5] "Excitation System Models for Power System Stability Studies," IEEE Transactions on Power Apparatus and Systems, Vol. PAS-100, No. 2, pp. 494-509, 1981 (Committee Report).
[6] IEEE Task Force on Overall Plant Response, “Dynamic Models for Steam and Hydro Turbines in Power System Studies”, IEEE Trans. on PAS, Vol PAS-92, Nov-Dec 1973, pp. 1904-1915.
[7] Task Force on Turbine-Governor Modeling, "Dynamic Models for Turbine-Governors in Power System Studies," IEEE Technical Report, PES-TR1, Jan. 2013.
[8] WECC M&VWG, "Composite Load Model for Dynamic Simulations" Ver 1.0, June 12, 2012.
[9] WECC M&VWG, "WECC Wind Power Plant Dynamic Modeling Guide," November 2010.
[10] EPRI, "Specification of the Second Generation Generic Models for Wind Turbine Generators," September 20, 2013. and WECC M&VWG, "Generic Solar Photovoltaic System Dynamic Simulation Model Specification," September 2012.
[11] WECC, "Generic Static Var System Models for the Western Electricity Coordinating Council" April 18, 2011.
[12] W. I. Rowen, “Simplified Mathematical Representations of Heavy Duty Gas Turbines”, ASME Paper 83‐GT‐63 and ASME Journal of Engineering for Power, October 1983, pages 865‐869. [GAST2A reference]
[13] Periera, L. et al, "A New Thermal Governing Approach in the WECC," IEEE Transaction on Power System, Vol. 18, No. 2, pp. 819-829, May 2003.
[14] WECC M&VWG, "Cross-current Compensation Model Specification," August 2015.
[15] EPRI, "Simple Model Specification for Battery Energy Storage System," March 6, 2015.
[W1] WECC Approved Dynamic Model Library. http://www.wecc.biz/
[W2] WECC M&VWG, "WECC Wind Power Plant Dynamic Modeling Guide," April 2014.
[W3] WECC M&VWG, "WECC PV Power Plant Dynamic Modeling Guide," April 2014.
[E1] EPRI, "Proposed Changes to the WECC WT3 Generic Model for Type 3 Wind Turbine Generators," September 27, 2013.
[E2] EPRI, "Proposed Changes to the WECC WT4 Generic Model for Type 4 Wind Turbine Generators," January 23, 2013.

## Additional links
Below are links to information that explains why some models are “unacceptable”.
Website
http://www.nerc.com/comm/PC/Pages/System-Analysis-and-Modeling-Subcommittee-(SAMS)-2013.aspx
Documents
http://www.nerc.com/comm/PC/NERCModelingNotifications/Modeling%20Notification%20–%20Use%20of%20GENTPJ%20Generator%20Model.pdf
http://www.nerc.com/comm/PC/NERCModelingNotifications/NERC%20Alert_EX2000%20-%20Final.pdf
http://www.nerc.com/comm/PC/NERCModelingNotifications/Notification%20Webinar%20–%20EX2000%20and%20GENTPJ%20–%20December%202016.pdf