## Slide 1: AEP’s Ground Grid Resistance Measurement Procedure

## Slide 2
Overview
Ground grid resistance (GGR) and GIC flow
Available approaches for obtaining GGR value
Calculating Effective GGR
A recommended procedure for obtaining GGR value

## Slide 3
Ground Grid Resistance and GIC Flow
1. Typical Substation ground grid
4/0 cu buried at 18”
10-20’ grid welded
Ground Rods every 20’ typical
Low R
Meets the requirement of IEEE80 standard

## Slide 4
2. Basic GIC flow

## Slide 5
3. The significance of GGR value on GIC calculation
Change in GIC values vs Substation GGR under different Thevenin ratio

## Slide 6
Obtaining GGR Value
1. Direct approach
Fall of potential (FOP)
Resistance
Distance
R

## Slide 7
  Most popular method for measuring sub station ground grid impedance
  Fixed test frequency range from 20 hertz to 418 hertz (50Hz and 60 Hz are omitted)
  To achieve 95% accuracy, it requires 6.5 times the grids maximum diagonal distance.
  Due to the impact of other interconnected ground sources, FOP should be performed only with new installation or the substation should be de-energized

## Slide 8
Clamp on meter

## Slide 9
  Theoretically it is able to measure the combination of substation ground grid and shield wire resistance
  The signal of clamp on meter is too weak to obtain an accurate measurement

## Slide 10
Computer based grounding multi-meter

## Slide 11
  Follows fundamental principles of the FOP method
  There are 1 current injection probe and 6 voltage probes
  Require less space for probe placement and does not need de-energize the substation.
  AEP’s field test has experienced inaccurate results. The vendor claimed they have improved the technique but requested additional funding. So AEP has stopped pursuing this approach

## Slide 12
Value form experience
  Last resort
  Based on experience, the value GGR range can be between 0.1 and 2 ohm.
  Our experience showed these default values can differ from actual values by up to 600%

## Slide 13
2. Indirect approach
USGS Survey
Wenner Method
IEEE 80
CDEGS Simulation
Step 1: Soil Resistivity
Step 2: Calculate GGR

## Slide 14
Soil Resistivity
= the resistivity of 1 cubic meter or 1 cubic centimeter soil. The unit of is ohm-m or ohm-cm

## Slide 15
Geological Survey
UNITED STATES DEPARTMENT OF AGRICULTURE Rural Electrification Administration REA BULLETIN 1751F-802

## Slide 16
Wenner Method
a = Distance between the electrodes
b = electrode depth
R = Reading in instrument
If a >20b the soil resistivity is calculated as:
Step 1: Soil Resistivity

## Slide 17
  Measurement can be taken outside of the energized station yard
  Can obtain site-specific, multi-layer values
  For reliable results, the test line must be longer than the diagonal length of the station yard.

## Slide 18
IEEE 80 (IEEE Guide for Safety in AC Substation Grounding)
A minimum value of the substation grounding system resistance in uniform soil can be estimated by means of the formula of a circular metal plate at zero depth
Where:
Substation ground grid resistance
Soil Resistivity in ohm-meter
A Area occupied by the ground grid in
(1)
Step 2: Calculating GGR

## Slide 19
Current Distribution, Electromagnetic Fields, Grounding and Soil Structure Analysis (CDEGS) Software
  Soil resistivity analysis and soil structure interpretation
  Arbitrary soil structures; any frequency & transients

## Slide 20
Station Name | Uniform Soil Layer Resistivity From USGS Survey (ohm*m) | CDGES - Wenner Method (ohm*m) | GGR Calculated by IEEE 80 method (ohms) | GGR From CDGES (ohms)
1 | 250 | 266.3481 | 1.812989 | 0.8
2 | 500 | 207.9795 | 2.145076 | 2.1438
3 | 500 | 41.43066 | 0.367745 | 724.17
4 | 500 | 74.35284 | 0.320555 | 0.59
5 | 250 | 202.9892 | 1.805878 | 4.11
6 | 250 | 934.514 | 5.662666 | 9.2347
7 | 66.67 | 84.61926 | 0.082047 | 0.3114
8 | 250 | 15.34106 | 0.10846 | 0.70856
9 | 500 | 1004.323 | 5.921809 | 4.0409
10 | 250 | 56.98275 | 0.142078 | 0.14
11 | 125 | 49.92627 | 0.056835 | 0.1086207
Comparison of USGS survey data and CDGES simulation results

## Slide 21
Comparison of different methods with per station cost
Method | Soil Resistivity Measurement Needed? | Station Ground Grid Model Required? | Requires De-Energized Station? | Cost ($/Station) |  | Accuracy
Effective GGR Direct measurement (Direct Approach) |  |  |  |  |  | 
Fall of Potential | No | No | Yes | $5,000 |  | High
Clamp On | No | No | No | $1,600 |  | Low
Computer based grounding multi-meter | No | Yes | No | $17,000 |  | Unconfirmed
GGR Measurement for Effective GGR Calculation (Indirect Approach) |  |  |  |  |  | 
Wenner method | Yes | No | No | $4000 | High | 
Survey | No | No | No | $0 | Low | 
IEEE 80 | No | Yes | No | $0 | Low | 
CDEGS | Yes | No | No | $1600 | High | 

## Slide 22
1. GIC flow with shield wire
It is standard AEP practice to connect station ground grids, either directly (with dedicated copper wires) or indirectly (through supporting steel structures) to the shield wires for lightning protection on high voltage transmission lines, which themselves are grounded at every transmission structure.
The shield wire grounding has provided an additional path for GIC propagation
Calculating Effective GGR

## Slide 23
Shield wire

## Slide 24
Effective GGR is the parallel of substation GGR and resistance of all overhead shield wires connecting to the substation ground grid.
Where:
Substation ground grid resistance
Equivalent grounding resistance of Xth shield wire
(2)
2. Calculating Effective GGR

## Slide 25
Shield wire is grounded through a conductor installed at each tower. It can be assumed as a series of Γ equivalent models shown below:
Where:
nth segment shield wire resistance
nth segment shield wire grounding resistance

## Slide 26
When there is only one Γ segment
When there are two Γ segments

## Slide 27
When there are three Γ segments:

## Slide 28
When there are n Γ segments:
=
Solving above equation gives:
is less than 0 which can be excluded. Therefore the Xth shield wire equivalent grounding resistance is calculated by . After calculating all shield wire equivalent ground resistance , the effective GGR is calculated by (2)
(3)

## Slide 29
Procedure for Obtaining GGR and Effective GGR values
Identify Substation List
GGR exist
Soil Resistivity
Wenner method
Estimate GGR CDEGS
Calculate
Effective GGR
GIC Calculation
YES
AEP’s recommendation
NO

## Slide 30
Questions?