## Slide 1
Distributed Energy Resources (DERs)
Reliability Impacts and Recommended Changes
Technical Advisory Committee (TAC)
May 25, 2017
Bill Blevins
Director, Grid Coordination

## Slide 2
Agenda
Background
Overview of DER whitepaper
Discussion of Reliability Impacts
Recommendations
Next Steps

## Slide 3: Background
Reliability White Paper Issued March 22, 2017
  http://www.ercot.com/content/wcm/lists/121384/DERs_Reliability_Impacts_FINAL.pdf
  Follow on to first DER Concept paper addressing markets
  Requested by TDSP’s in response to ERCOT’s request for additional information
  ERCOT started writing the DER reliability whitepaper after the DREAMTF concluded their work in 1st qtr 2016.
  Very Similar in scope to NERC whitepaper issued Feb 2017
“Based on installed capacity and current rates of growth, these resources do not pose an immediate or near-term reliability concern for the transmission grid. “
Notes: ERCOT started writing the DER reliability whitepaper after the DREAMTF concluded their work in 1st qtr 2016.

## Slide 4: Overview DER Whitepaper
DER Introduction
Reliability Concerns
Transition Activities-Recommendations
Pending rules-Other Activities
Notes: ERCOT started writing the DER reliability whitepaper after the DREAMTF concluded their work in 1st qtr 2016.

## Slide 5: Section 2. Definitions
Distributed Energy Resource
  Generation, energy storage technology, or a combination of the two that is interconnected at or below 60 kV and operates in parallel with the distribution system. (Does not include demand response.)
Connected Capacity
  The output capability of a Distributed Generation (DG) facility before applying any protective or operational limitations. This is most often the nameplate capability of the generating system or the rated capability of the inverter.
Operating Capacity
  The output capability approved by the Distribution Service Provider for parallel operations with the utility system. In some cases, customers operate their DG Facilities with only a portion of the Connected Capacity at a given point in time. Other customers may have spare generating capacity and limit what is used at a given point in time.

## Slide 6: Section 3. Reliability Impacts
Power Flow and State Estimation (SE)
  Incorrect handling of energy injection data from distribution circuits may lead to invalid SE results, inaccurate Load Adaptation and hence incorrect Load Distribution Factors (LDFs) in Operational Studies;
Load Forecast
  Inaccuracies Short-Term and Mid-Term Load Forecast may lead to excessive dependance on reserves;
  Inaccuracies in forecasting DERs used Long-Term Load Forecast may lead to less than optimal transmission planning decisions;
Limited reactive power, voltage control, and lacking dynamic response to faults may affect grid reliability during abnormal system disturbances.
Lack of coordination during system restoration of DER energization following a system blackout may cause power quality issues.

## Slide 7: Section 4. Recommendations
ERCOT
  Collect CIM Load locations for existing registered DERs >1 MW
    Now 99 Registered DERs as of May 1, 2017
    20 new since November, 2016
  Develop a means to map registered DER to CIM Load
  Allow TDSPs flexibility to modify CIM Loads as required
TDSPs (including NOIEs)
  Continue to monitor unregistered DER.
ERCOT and TDSPs
  Jointly develop thresholds for “accumulations” of DER
  Report accumulations of DERs that exceed the threshold
  Map “clusters” > threshold to a CIM load

## Slide 8: Section 4.1. Potential System Changes
Gather data on registered DERs from all parties in a consistent manner.
Map to CIM in collaborative process by type.
Revise the ERCOT SE to allow injections from specific loads.
Revise ERCOT's Load Adaptation to track and estimate DER schedules at CIM Loads where DERs are mapped.
Forecast intermittent DER as it builds out in specific areas.
Update STLF and MTLF to accommodate intermittent DER forecasts.
Integrate DER forecast into SCED in the GTBD.
Update Long Term forecast procedures to account for DER.
Incorporate additional contingency definitions to account for DER impacts.

## Slide 9: Section 4.2. Monitoring Growth and Developing Thresholds
Establish process for monitoring overall growth of DER
Establish criteria for the thresholds to map accumulations of unregistered DER
Notes: DER today does not pose a threat but the rate of growth of un-registered DER will drive the urgency for specific recommendations

## Slide 10: Section 5. Ongoing Efforts to address DER reliability concerns
IEEE 1547-2017
  Voltage Regulation & Reactive Power (2 Performance Categories)
  Frequency-Droop Capability (Based on ERCOT Rules)
  Frequency Ride-Through
  Voltage Ride-Through (3 Performance Categories)
  Return to Service after Trip (an intentional delay & max ramp rate)
FERC NOPR Docket No. RM16-8-000
  Small Generators (no larger than 20 MW) to ride-through abnormal frequency and voltage events, and avoid disconnecting during such events

## Slide 11
Future Activities

## Slide 12: DER Reliability Whitepaper next steps
Collect additional data on Existing Registered DERs
Insert these DERS into the Network Model as new resources mapped to their CIM load points.
  Once in the model, the DGs’ locations will be known to operators in the ERCOT control room, improving our situational awareness
Establish binding language to incorporate mapping of future registered DER and incorporate into ERCOT systems

## Slide 13: DER mid-term steps
Establish process for monitoring overall growth of non-registered DER in ERCOT
  Will not require formal reporting.
  Work with TDSPs on triggers for mapping localized accumulations

## Slide 14: DER future steps
Monitor IEEE standards for final rules
Study impacts of DER based on IEEE standards
Determine if IEEE standards will be sufficient
Establish binding language with TDSPs to report accumulations of non-registered DER and incorporate into ERCOT systems