## Slide 1
Far West Texas Transmission Project -
ERCOT Independent Review
TAC
May 25, 2017

## Slide 2: Overview
AEPSC and Oncor jointly submitted Far West Texas Project (FWTP) for Regional Planning Group review. The original AEP and Oncor proposal was a Tier 1 project that was estimated to cost $ 423 million.
  Proposed for 2021 to 2022 timeframe
  Addresses oil and gas related load growth
  Reliability Issues
    Voltage Collapse
    Loss of Load
    Short-Circuit Strength & System Protection
  Provide Operational Flexibility
  Provides future upgrade path for Far West Region

## Slide 3: Steady State & Dynamics Results
Steady State | Study Case* | No Solar Case**
Unsolvable Contingencies | One (in Culberson loop) | One (in Culberson loop)
Thermal Violations | One 138 kV line (32 miles; Rio Pecos, TNMP 16TH St. region) | Four 138 kV lines (total 52 miles; Rio Pecos, TNMP 16TH St. region)
Voltage Violations | 18 – 138 kV buses in Culberson | 11 – 138 kV buses in Culberson
Voltage Deviations | None | 10 – 138 kV buses
Transient Stability | Study Case | No Solar Case
Voltage Recovery Violations | P6, P7 | P4, P6, P7
* 533 MW load in Culberson Loop, 511 MW load in Barilla Junction area
** 0 MW solar in the study region and 6% load reduction in Far West to reflect no solar peak period

## Slide 4: Initial Project Options Evaluation
Nearly 40 project alternatives were studied
  Initial options included subset of transmission elements from the Oncor & AEP proposal
  Initial Options were screened and shortlisted based on:
    Steady State Analysis
    Voltage Stability Analysis (PV results)
    Load Serving Capability including ability to meet future load growth
    Project Cost estimate
    ROW impact
    Cost of upgrading existing lines to relieve overloads
Based on the initial options screening, four options (included in Appendix) were selected for detailed analysis

## Slide 5: Final Options - Overall Comparison
Description | Option 1 | Option 2 | Option 3 | Option 4
System Performance – Study Case | Met criteria | Met criteria | Met criteria | Met criteria
System Performance – Potential Load Case* | Criteria not Met | Criteria not Met | Met criteria | Met criteria
Capital cost ($ Million) | 464 | 336 | 446 | 501
PV Results Culberson Load Served | 917 | 717 | 917 | 1037
Relative Production Cost Savings ($ Million) | - | 6.2 | 6.6 | 6.6
Total System Loss Reduction (MW) | 10.4 | 31.2 | 34.4 | 34.4
New Right of Way Required | 187 mi | 169 mi | 235 mi | 235 mi
* 834 MW load in Culberson Loop, 568 MW load in Barilla Junction area

## Slide 6: Sensitivity Analysis – PG Section 3.1.3 (4)
ERCOT concludes that the generation sensitivity analysis as described in PG Section 3.1.3 (4)(a) did not have an impact on the project need and any of the four project options
A review of the Power Transfer Distribution Factors (PTDFs) of overloaded elements with respect to the load transfer for each weather zone (excluding Far West) concludes that the load scaling as described in PG Section 3.1.3 (4)(b) did not have impact on the project need and any of the four project options

## Slide 7: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse Option 2 to address the reliability need in the study region:
  Expand the Riverton Sw. Sta. to install a 345 kV ring-bus arrangement with two 600 MVA, 345/138 kV autotransformer
  Construct a new approximately 85-mile 345 kV line on double-circuit structures with one circuit in place, between Moss and Riverton Sw. Sta. Add a second circuit to the existing 16-mile Moss Sw. Sta. – Odessa EHV 345 kV double-circuit structures. Install 345 kV circuit breaker(s) at Odessa EHV. Connect the new circuit from Riverton Sw. Sta. and terminate at Odessa EHV to create the new Odessa EHV – Moss - Riverton 345 kV Line
  Expand the Solstice Sw. Sta. to install a 345 kV ring-bus arrangement with two 600 MVA, 345/138 kV autotransformer
  Construct a new approximately 68-mile 345 kV line from Solstice Sw. Sta. to Bakersfield station on double-circuit structures with one circuit in place
Estimated Capital Cost: $336 million

## Slide 8: Option 2
?

## Slide 9
Appendix

## Slide 10: Option 1 – Results
Odessa EHV
Riverton
Fort-Stockton
N. McCamey
Culberson
SC (200 MVAR)
Cap Banks
SC
Proposed synchronous condenser
SC (200 MVAR)
Mentone
Reliability Assessment | Study Case | Potential Load
PV (Culberson Load) | 917 (P6) 927 MW (P7) | 
Thermal | Study Case : No Violations No Solar Case : No Violations | Study Case : Violations No Solar Case : Violations
Voltage Violation | Study Case : No Violations No Solar Case : No Violations | Study Case : No Violations No Solar Case : No Violations
Estimated Cost $464 Million
Pig Creek
Cap bank at Mentone and SaltCreek | 36 MVARs each
Cap bank at Orla and Elmar, Loving | 18 MVARs each
Cap bank at ALMC | 18 MVARs
Cap bank at ESPY, SHAF, TSAND | 3.6,10.8, and 7.2 MVARS
Sand Lake
345 kV construction operating at 138 kV

## Slide 11: Option 2 - Results
Odessa EHV
Riverton
Solstice
Bakersfield
2 XFRMs
2 XFRMs
Proposed 345 kV circuit
XFRM
Proposed 345/138 transformer
Reliability Assessment | Study Case | Potential Load
PV (Culberson Load) | 717 MW (P7) 767 MW (P1, ERCOT X-1+N-1) | 
Thermal | Study Case : No Violations No Solar Case : No Violations | Study Case : Violations No Solar Case : Violations
Voltage Violation | Study Case : No Violations No Solar Case : No Violations | Study Case : Violations No Solar Case : Violations
Estimated Cost $336 Million

## Slide 12: Option 3 - Results
Odessa EHV
Riverton
Solstice
Bakersfield
Sand Lake
2-XFRMs
2-XFRMs
XFRM
Proposed 345/138 transformer
Reliability Assessment | Study Case | Potential Load
PV (Culberson Load) | 917 MW (ERCOT X-1+N-1) 967 MW (P7) | 
Thermal | Study Case : No Violations No Solar Case : No Violations | Study Case : No Violations No Solar Case : No Violations
Voltage Violation | Study Case : No Violations No Solar Case : No Violations | Study Case : No Violations No Solar Case : No Violations
Estimated Cost $446 Million
1-XFRM
Proposed 345 kV circuit
RPG approved 345 kV line
operated @ 138 kV

## Slide 13: Option 4 – Results
Odessa EHV
Riverton
Solstice
Bakersfield
Sand Lake
2-XFRMs
XFRM (x2)
Proposed 345 kV circuit
SC
Proposed synchronous condenser
XFRM
Proposed 345/138 transformer
Reliability Assessment | Study Case | Potential Load
PV (Culberson Load) | 1037 MW (P6, ERCOT X-1+N-1) 1137 MW (P7) | 
Thermal | Study Case : No Violations No Solar Case : No Violations | Study Case : No Violations No Solar Case : No Violations
Voltage Violation | Study Case : No Violations No Solar Case : No Violations | Study Case : No Violations No Solar Case : No Violations
Estimated Cost: $501 Million
1-XFRMs
Culberson
SC (200 MVAR)
RPG approved 345 kV line
operated @ 138 kV

## Slide 14: Culberson Loop & Barilla Junction Area Loads
Historic and Projected Summer Peak Loads from the original AEPSC & Oncor RPG submittal
Projected 2021 Summer Peak Loads following Oncor & AEPSC updates
  Updated Feb. 2017
    Culberson Loop area: 533 MW *
    Barilla Junction area: 511 MW *
  Updated May 2017
    Culberson Loop area: 582 MW
          *Summer Peak Loads used in the ERCOT Independent Review