## Slide 1
Series Capacitors Update
TAC
May, 2017

## Slide 2: NPRR562 Timeline
May TAC
June
BOD
July
Effective

## Slide 3: Series Capacitors with No SSR Risk (Place In Service)
Valley
Kopperl
Romney

## Slide 4: Series Capacitors with SSR Risk within N-4 (Bypass)
Edison / Oersted
(Bypass Edison or Oersted)
Gauss (1)

## Slide 5: Series Capacitors with SSR Risk N-5 or N-6 (Place In Service and Monitor)
Edison / Oersted
(Bypass Edison or Oersted)
Kirchhoff
Gauss (1)
Cross

## Slide 6: Operation Monitoring and Outage Coordination (N-5/N-6 Risk)
Three Contingencies away from SSR vulnerability
Normal Operation (Review Action Plan)
Two Contingencies away from SSR vulnerability
Implement Action Plan
The ERCOT EMS system will be utilized to monitor transmission outages
A double circuit transmission outage is considered as one contingency in Operations

## Slide 7: Series Capacitor Operation
Initially, placing series capacitors in-service will improve Panhandle GTC export capability ~150 MW
In process of sharing operating plan with REs of units N-5 and N-6 vulnerable
Will coordinate with TSPs to identify transmission options for generators with SSR vulnerability within N-4 outages

## Slide 8: Acknowledgement
ERCOT Resource Entities
Developers, Vendors
Consultants, Expertise
ERCOT Transmission Planners, Operators