## Slide 1
ERCOT-SPP Coordinated
Lubbock Power and Light
Integration Impact Study Results
Jeff Billo
May 25, 2017

## Slide 2: Background
In June 2016, ERCOT completed Lubbock Power and Light (LP&L) Integration Study (filed in PUCT Project 45633)
In July 2016, memo from Former Chairman Nelson asked for ERCOT-SPP coordinated study of the impacts of an LP&L transition to ERCOT
In November 2016, ERCOT presented draft study scope and assumptions to RPG (http://www.ercot.com/content/wcm/key_documents_lists/77750/SPP_ERCOT_Lubbock_Scope_RPG_11_15_2016.pdf)
In February 2017, SPP and ERCOT finalized the study scope (filed in PUCT Project 45633)

## Slide 3: ERCOT LP&L Integration Study (June 2016)
ERCOT preferred Option 4ow for integrating the LP&L system
$364 million capital cost estimate

## Slide 4: Results
The following slides will summarize the preliminary results of the analysis performed as part of the study scope
Final and detailed information will be available in the study report ERCOT plans to file with the PUCT in June
SPP is expected to file a separate report for their portion of the study scope

## Slide 5: ERCOT production cost analysis
Year | Panhandle Interface Limit* | Production cost increase due to the addition of LP&L System into ERCOT
2020 (without LP&L) | 3629 MW | -
2020 (with LP&L) | 4067 MW | $66 million
2025 (without LP&L) | 3629 MW | -
2025 (with LP&L) | 4067 MW | $60 million
* Set at 90% of WSCR Stability Limit; Limit assumed no LP&L units online
Addition of load to ERCOT system causes increase in production cost (note: production cost numbers do not take into account payment from load)
Production cost increase from load partially offset by decrease in Panhandle export congestion due to transmission assumed to connect LP&L
Above numbers to be compared with SPP production cost decrease in order to determine overall production cost impact
PRELIMINARY RESULTS

## Slide 6: ERCOT avoided project analysis
The 2016 Regional Transmission Plan identified the need to add a synchronous condenser at Windmill by 2019
ERCOT’s analysis showed that if LP&L were integrated into ERCOT in 2021, it would still be economic to add a synchronous condenser at Windmill by 2019
PRELIMINARY RESULTS

## Slide 7: Operational cost and reliability impact assessment
LP&L integration would introduce a new voltage level (115kV) into the ERCOT system, so modeling, documentation, and rules (for example, shadow price cap) will need to be updated
ERCOT’s preferred LP&L integration Option 4ow transmission will strengthen Panhandle system increasing transient and voltage stability
PRELIMINARY RESULTS

## Slide 8: Ancillary services impact assessment
ERCOT evaluated LP&L integration impact on Regulation-Up, Regulation-Down, Responsive Reserve Service, and Non-spin Reserve Service
LP&L load will contribute to paying the cost of Ancillary services
Impacts are expected to be minimal. The below charts show the delta on Regulation requirements:
PRELIMINARY RESULTS
MW
MW

## Slide 9: Congestion rights impact analysis
May have an impact on CRR values
If LP&L does not opt into creating a separate Load Zone and is instead absorbed into an existing Load Zone, values for CRRs sourcing and sinking in that existing Load Zone will be affected for those sold for future years
LP&L integration decision may be made prior to affected auctions
PRELIMINARY RESULTS

## Slide 10: Subsynchronous resonance impact analysis
23 generators had an increase in the number of outages required to be radial to a series capacitor
  These generators would have less SSR risk
  None of these generators went from less than or equal to 6 outages to more than 6 outages from radial condition
5 generators went from 20 outages to 14 outages to be radial to Edison/Oersted series capacitors
  All 5 are significantly far away from Edison/Oersted series capacitors
  All of these generators (Panhandle) already have SSR mitigation and/or protection in place
PRELIMINARY RESULTS

## Slide 11: Analysis of whether or not to convert retiring LP&L generators to synchronous condensers
ERCOT found production cost savings that would justify the cost of converting retiring LP&L Coke Units 1 and 2 to synchronous condensers in 2025 (not found to be economic in 2020)
However, the overall impact on the Panhandle interface limit was less than 100 MW and installing new synchronous condensers at selected locations within the Panhandle would provide better economic benefit
ERCOT will not recommend converting LP&L units to synchronous condensers
PRELIMINARY RESULTS

## Slide 12: Next steps
Finalize results and present to the Board on June 13
File final report with the PUCT

## Slide 13
Questions?