## Slide 1
Rayburn Electric Cooperative Load Integration Study
TAC
May 25, 2017

## Slide 2: Background
Rayburn Electric Cooperative (RCEC) is considering connecting the remainder of its load, approximately 190 MW (no generation), to the ERCOT Grid as early as December 2019
Rayburn and Lone Star Transmission performed their own study & identified preferred options
PUCT instructed ERCOT to study the impact of integrating RCEC into the ERCOT Grid
Objective to identify transmission facilities that will be required to integrate the Rayburn load and transmission network into the ERCOT Grid and satisfy ERCOT and NERC Transmission Planning reliability standards in the most efficient way possible
RCEC Load Integration Scope and Assumptions:
  http://www.ercot.com/calendar/2016/9/20/77741-RPG

## Slide 3: Approach
PROJECT OPTIONS
STEADY STATE ANALYSIS
(N-1, G-1+N-1, X-1+N-1)
CHECK FOR CONSTRAINTS AND VIOLATIONS
PRODUCTION COST ANALYSIS (UPLAN)
OPTIONS COMPARISON BASED ON PROJECT COST
ERCOT RECOMMENDATION

## Slide 4: Options Evaluation
ERCOT evaluated 12 Options using the following criteria:
  NERC/ERCOT Reliability criteria
  345 kV connectivity feasibility
  Capital cost consideration
  Ease of building new substation or expanding existing ones
Based on the evaluation, four shortlisted options (included in Appendix) were selected for detailed analysis

## Slide 5: ERCOT Recommendation
Based on the study, ERCOT recommends Option 2 as the most efficient alternative for integrating the RCEC load into ERCOT
  Meets applicable reliability criteria with significant margin for future load growth
  Least cost option
  Annual production costs values close and comparable to other options

## Slide 6: Option 2 – Capital cost estimate : $38 Million
RCEC system – Yellow buses
345 kV Tap and Auto
138 kV bus extension
New 138 kV connection (0.5 mile)
0.9 mile 138 kV connection

## Slide 7: Option 2 – Project Description
Extend Bus Work & add 138kV jumper (<0.1 mile) to connect Canton Switch Station to Canton Tap
New 345kV Substation (6 breaker ring bus) on one circuit of Martin Lake – Tricorner line app. 83 miles from Martin Lake (Aristotle_345 Sub)
New 138kV Switching Station on the 138kV Teaselville - Palestine line app. 30 miles from Palestine (Apollo_138)
345/138kV, 650 MVA auto at Aristotle
New 0.9 mile single circuit 138kV line from Aristotle to Ben Wheeler
Expand Ben Wheeler sub to accommodate Aristotle_345 Sub & Canton Sub connection
Extend the 138kV Coffee - Jacksonville single circuit line into the new Apollo_138kV switching station (0.5 miles)

## Slide 8: Questions?

## Slide 9: Appendix

## Slide 10: Option 1 – Capital cost estimate: $39 Million
RCEC system – Yellow buses
345 kV Tap and Auto
138 kV bus extension
New 138 kV connection (0.5 miles)
0.5 mile 138 kV connection

## Slide 11: Option 2 – Capital cost estimate : $38 Million
RCEC system – Yellow buses
345 kV Tap and Auto
138 kV bus extension
New 138 kV connection (0.5 mile)
0.9 mile 138 kV connection

## Slide 12: Option 3 - Capital cost estimate: $48 Million
RCEC system – Yellow buses
345 kV Tap and Auto
138 kV bus extension
New 138 kV connection (8.4 miles)
0.5 mile 138 kV connection

## Slide 13: Option 4 - Capital cost estimate: $47 Million
RCEC system – Yellow buses
345 kV Tap and Auto
138 kV bus extension
New 138 kV connection (8.4 miles)
0.9 mile 138 kV connection