## Sheet1
RARF v5.4 Validation Rule Comments
Form | Tab | Error or Warning | Fix or Enhancement | Element | Message | Comments/Suggestions
Gen | Parameters | W | E | High Reasonability Limit | HRL is > Real Power Rating | This is a mis-application of the HRL. It is a theoretical value, and SHOULD BE > the Real Power Rating. Rule doesn't exist in Validation Rules spreadsheet, suggest getting rid of the ghost rule.
Gen | Protection | W | F | Under/Overvoltage 1 | Value is blank but required | Not all plants HAVE under/over voltage protection, and it is not required by Protocols/Operating Guides. Suggest removing first validation rule
Gen | Protection | W | F | Under/Overvoltage 1 Time | Value is blank but required | Not all plants HAVE under/over voltage protection, and it is not required by Protocols/Operating Guides. Suggest modifying first validation rule to fire only if Under/Over Voltage 1 is not null
Gen | Protection | E | F | Under/Overvoltage 2, 3, & 4 | Value (NULL) must be numeric > 0 | Not all plants have more than one under/over voltage trip. Suggest modifying rule 2 to only error if cell is not null
Gen | Protection | E | F | Underfrequency 1, 2, 3, & 4 Time | Value (0.05) must be numeric = 0 for UF (57.47) | Suggestion: Delete rule #6. Rule is not supported by Operating Guides, there is no maximum time required
Gen | Protection | E | F | Overfrequency 1, 2, 3, & 4 Time | Value (0.05) must be numeric = 0 for OF (62.43) | Suggestion: Delete rule #5. Rule is not supported by Operating Guides, there is no maximum time required
Gen | Reactive Capability Curve | W | E | MW5 Unity Power Factor | Value must be > HRL | This is a misapplication of the HRL, and serves no purpose. Suggest deleting rule #3
Gen | Reactive Capability Curve | W | E | MW1 | Value should be < LRL | Misapplication of LRL. Validation rule #3 fires off of WMN (unit minimal output), which is an undefined term. Suggest reporgramming rule to fire off of LSL instead
Gen | Reactive Capability Curve | W | E | MW1 | Value should be < unit min output | Rules 1 and 3 conflict when unit min output is 0.0 MW
Transmission | Transformer Data | W | E | Positive Sequence Reactance | Reactance may be rounding. Value has a precision less than 5 decimal places | Suggest doing something about a 5 decimal place value than ends with a zero
Transmission | Transformer Data | W | E | Low Side Nominal Voltage | Low side voltage is >5% deviation of 69, 138, 230, or 345 kV | Low side voltage is ALWAYS going to be >5% of 69, 138, 230, or 345kV, otherwise there'd be no reason to have a transformer. Suggest deleting rule 32 and change rule #3 from a warning, to an error.
Transmission | Load Data | W | E | Device Name | Connected device must also exist in Breaker/Switch tab | If the connected device is not owned by the RE, it cannot be in the breaker/switch tab. If connected device is a transformer, it cannot be in the breaker switch tab. If connected device is a line, it cannot be in the breaker/switch tab. If connected device is a load, it cannot be in the breaker/switch tab. Suggest deleting rule #4.
Transmission | Breaker/Switch Info | W | E | Normal Operating Status | Should be closed for units to operate in the market | Not true for all cases. Suggest evaluating the deletion or modification of this rule
Transmission | Transformer Data | W | F | High/Low Side Voltage Connected Devices |  | If the connected device is not owned by the RE, it cannot be in the breaker/switch tab. If connected device is another transformer, it cannot be in the breaker switch tab. If connected device is a load, it cannot be in the breaker/switch tab. Suggest deleting rule #3.
Transmission | Transformer Data | W | E | Automatic Voltage Regulation | AVR should be "Y" if Total Number of Tap Positions > 16 | Why? Suggest deleting rule #3
Transmission | Transformer Data | W | E | Continuous Rating | Continuous rating should be > HRL | Misapplication of HRL. Suggest modifying rule #4 to reference HSL instead of HRL
Renewable | Unit Info | E | F | Average Height Panel Center | Value must be numeric > 0 | Validation rule does not exist
General Comments on Validation Rule Document
Delete the word "Instantaneous" from under/over voltage/frequency trip 1,2,3, & 4
Validation rule document shows a combined Wind/Solar Photovoltaic form. Form does not exist
Validation rule document shows both a Wind, and a Solar Photovoltaic form. Forms do not exist, RARF has a Renewable form
No validation rules exist for several Unit Info elements for Renewable. This needs some serious cleanup.