## Slide 1: CRR/PTP Trading Restrictions
As proposed by NPRR 832

## Slide 2: PUN Contingency Definitions
Contingencies at a PUN bus do not consider
1. PUN operator response, or
Load-Resource dependencies (e.g. process steam)
For example, G-1 contingencies, that may be managed by the PUN, are not adequately considered in constraint definitions.

## Slide 3: PUN Contingency Definitions Example
PUN
~
Outage on 100MVA Line
100MVA Line
125MW Load
100 MW Resource
In this example (which occurred, and contributed to RENA), the PUN is radial to the ERCOT system due to a scheduled outage. ERCOT enforced a G-1 contingency on the PUN resource to recognize, on a post-contingent basis, the PUN load could not be served by the radial line connecting the PUN to the ERCOT system. The Bus was priced at the shadow price cap, and did not impact the load zone price (LDF = 0.)

## Slide 4: PUN Contingency Definitions Example
PUN
~
Outage on 100MVA Line
100MVA Line
125MW Load
100 MW Resource
In reality, the PUN operator may:
Have consequential load that depends on steam to continue a process. Consequential load may reduce consumption following a resource contingency, or
Recognize that, post-resource contingency, the ERCOT system will be unable to serve plant load. Rather than risk relay / overcurrent separation from the ERCOT system, the operator may choose to manually manage PUN load at or below the line rating (similar to a RAP)
Steam

## Slide 5: Complications with PUN Contingency Updates
One size does not fit all
Load-Resource Dependencies may be commercially sensitive
Ability to reduce load may be commercially sensitive

## Slide 6: ERCOT ignores constraints for existing PUNS
A PUN resource with a local mitigation plan allowed ERCOT to de-activate an otherwise binding constraint (May 2017.)